## Fault Current Calculator
Project Name
Firm Name
Date
Engineer
Estimated Available Fault Current Calculator
MAIN |  |  | FEEDER | BRANCH
Name |  |  | Name | Name
Secondary Voltage
Total System Motor Load (HP)
Primary Available Fault Current (A)
Primary Voltage
Transformer Rating (kVA)
Nameplate Transformer Impedance (%Z)
Rated Secondary Current (A) |  | 0
or
Secondary Available Fault Current (A)
Conductor Length (ft.)
Size of Conductors
Copper
Aluminum
In Conduit
Cable
Steel
Non-Magnetic
Number of Sets
Fault Current Available (A)
NOTE: This program estimates available fault currents for three phase systems. The calculation of motor contribution in this
calculator is approximate only - systems with large motor contribution, high X/R conditions, closed transition paralleled sources
or high impedance grounding will require a more accurate calculation method. Please see Application Hints for more information.
[5 empty] | CA2 | CC2 | SN2 | COND2 | SETS2 | I2 | F2 | M2 | C2 | Column | FCA2 |  | CA3 | CC3 | SN3 | COND3 | SETS3 | I3 | F3 | M3 | C3 | Column | FCA3
[5 empty] | 1 | 1 | 1 | 13 | 1 |  | #VALUE! | #VALUE! | 15082 | 3 |  |  | 1 | 1 | 1 | 9 | 1 |  | #VALUE! | #VALUE! | 7292 | 3
[5 empty] | FEEDER | [11 empty] | BRANCH
[7 empty] | mag | nonmag | mag | nonmag | cable mag | cbl nonmag | cable mag | cbl nonmag |  |  |  |  | mag | nonmag | mag | nonmag | cable mag | cbl nonmag | cable mag | cbl nonmag
[5 empty] | pos | size | copper | copper | aluminum | aluminum | copper | copper | aluminum | aluminum |  |  | pos | size | copper | copper | aluminum | aluminum | copper | copper | aluminum | aluminum
[5 empty] | 1 | 14 | 389 | 389 | 236 | 236 | 389 | 389 | 236 | 236 |  |  | 1 | 14 | 389 | 389 | 236 | 236 | 389 | 389 | 236 | 236
[5 empty] | 2 | 12 | 617 | 617 | 375 | 375 | 617 | 617 | 375 | 375 |  |  | 2 | 12 | 617 | 617 | 375 | 375 | 617 | 617 | 375 | 375
[5 empty] | 3 | 10 | 981 | 981 | 598 | 598 | 981 | 981 | 598 | 598 |  |  | 3 | 10 | 981 | 981 | 598 | 598 | 981 | 981 | 598 | 598
[5 empty] | 4 | 8 | 1557 | 1558 | 951 | 951 | 1559 | 1559 | 951 | 951 |  |  | 4 | 8 | 1557 | 1558 | 951 | 951 | 1559 | 1559 | 951 | 951
[5 empty] | 5 | 6 | 2425 | 2430 | 1480 | 1481 | 2431 | 2433 | 1481 | 1482 |  |  | 5 | 6 | 2425 | 2430 | 1480 | 1481 | 2431 | 2433 | 1481 | 1482
[5 empty] | 6 | 4 | 3806 | 3825 | 2345 | 2350 | 3830 | 3837 | 2351 | 2353 |  |  | 6 | 4 | 3806 | 3825 | 2345 | 2350 | 3830 | 3837 | 2351 | 2353
[5 empty] | 7 | 3 | 4760 | 4802 | 2948 | 2958 | 4760 | 4802 | 2948 | 2958 |  |  | 7 | 3 | 4760 | 4802 | 2948 | 2958 | 4760 | 4802 | 2948 | 2958
[5 empty] | 8 | 2 | 5906 | 6044 | 3713 | 3729 | 5989 | 6087 | 3733 | 3739 |  |  | 8 | 2 | 5906 | 6044 | 3713 | 3729 | 5989 | 6087 | 3733 | 3739
[5 empty] | 9 | 1 | 7292 | 7493 | 4645 | 4678 | 7454 | 7579 | 4686 | 4699 |  |  | 9 | 1 | 7292 | 7493 | 4645 | 4678 | 7454 | 7579 | 4686 | 4699
[5 empty] | 10 | 1/0 | 8924 | 9317 | 5777 | 5838 | 9209 | 9472 | 5852 | 5879 |  |  | 10 | 1/0 | 8924 | 9317 | 5777 | 5838 | 9209 | 9472 | 5852 | 5879
[5 empty] | 11 | 2/0 | 10755 | 11423 | 7186 | 7301 | 11244 | 11703 | 7327 | 7372 |  |  | 11 | 2/0 | 10755 | 11423 | 7186 | 7301 | 11244 | 11703 | 7327 | 7372
[5 empty] | 12 | 3/0 | 12843 | 13923 | 8826 | 9110 | 13656 | 14410 | 9077 | 9242 |  |  | 12 | 3/0 | 12843 | 13923 | 8826 | 9110 | 13656 | 14410 | 9077 | 9242
[5 empty] | 13 | 4/0 | 15082 | 16673 | 10740 | 11174 | 16391 | 17482 | 11184 | 11408 |  |  | 13 | 4/0 | 15082 | 16673 | 10740 | 11174 | 16391 | 17482 | 11184 | 11408
[5 empty] | 14 | 250 | 16483 | 18593 | 12122 | 12862 | 18310 | 19779 | 12796 | 13236 |  |  | 14 | 250 | 16483 | 18593 | 12122 | 12862 | 18310 | 19779 | 12796 | 13236
[5 empty] | 15 | 300 | 18176 | 20867 | 13909 | 14922 | 20617 | 22524 | 14916 | 15494 |  |  | 15 | 300 | 18176 | 20867 | 13909 | 14922 | 20617 | 22524 | 14916 | 15494
[5 empty] | 16 | 350 | 19703 | 22736 | 15484 | 16812 | 19557 | 22736 | 15413 | 16812 |  |  | 16 | 350 | 19703 | 22736 | 15484 | 16812 | 19557 | 22736 | 15413 | 16812
[5 empty] | 17 | 400 | 20565 | 24296 | 16670 | 18505 | 24253 | 26915 | 18461 | 19587 |  |  | 17 | 400 | 20565 | 24296 | 16670 | 18505 | 24253 | 26915 | 18461 | 19587
[5 empty] | 18 | 500 | 22185 | 26706 | 18755 | 21390 | 26980 | 30028 | 21394 | 22987 |  |  | 18 | 500 | 22185 | 26706 | 18755 | 21390 | 26980 | 30028 | 21394 | 22987
[5 empty] | 19 | 600 | 22965 | 28033 | 20093 | 23451 | 28752 | 32236 | 23633 | 25750 |  |  | 19 | 600 | 22965 | 28033 | 20093 | 23451 | 28752 | 32236 | 23633 | 25750
[5 empty] | 20 | 750 | 24136 | 28303 | 21766 | 23491 | 31050 | 32404 | 26431 | 25682 |  |  | 20 | 750 | 24136 | 28303 | 21766 | 23491 | 31050 | 32404 | 26431 | 25682
[5 empty] | 21 | 1000 | 25278 | 31490 | 23477 | 28778 | 33864 | 37197 | 29864 | 32938 |  |  | 21 | 1000 | 25278 | 31490 | 23477 | 28778 | 33864 | 37197 | 29864 | 32938
[5 empty] | 1 |  | 7 | 3 | [8 empty] | 1 |  | 7 | 3
[5 empty] | 2 |  | 8 | 5 | [8 empty] | 2 |  | 8 | 5
[5 empty] | 3 |  | 9 | 7 | [8 empty] | 3 |  | 9 | 7
[5 empty] | 4 |  | 10 | 9 | [8 empty] | 4 |  | 10 | 9
[5 empty] | 5 |  | 11 | 4 | [8 empty] | 5 |  | 11 | 4
[5 empty] | 6 |  | 12 | 6 | [8 empty] | 6 |  | 12 | 6
[5 empty] | 7 |  | 13 | 8 | [8 empty] | 7 |  | 13 | 8
[5 empty] | 8 |  | 14 | 10 | [8 empty] | 8 |  | 14 | 10
[5 empty] | CA1 | CC1 | SN1 | COND1 | SETS1 | I1 | F1 | M1 | C1 | V1 | V | AIC T
[5 empty] | 1 | 1 | 1 | 18 | 1 |  | #DIV/0! | #DIV/0! | 22185 | 2 | 208 | #DIV/0! |  |  | Known Primary Fault Current
SERVICE
[7 empty] | mag | nonmag | mag | nonmag | cable mag | cbl nonmag | cable mag | cbl nonmag |  | Column |  |  |  | Vp |  | f
[5 empty] | pos | size | copper | copper | aluminum | aluminum | copper | copper | aluminum | aluminum |  | 3 |  |  |  | 0 |  | #DIV/0!
[5 empty] | 1 | 14 | 389 | 389 | 236 | 236 | 389 | 389 | 236 | 236
[5 empty] | 2 | 12 | 617 | 617 | 375 | 375 | 617 | 617 | 375 | 375 |  | FCA |  |  |  | Vs |  | M
[5 empty] | 3 | 10 | 981 | 981 | 598 | 598 | 981 | 981 | 598 | 598 | [5 empty] | 208 |  | 1
[5 empty] | 4 | 8 | 1557 | 1558 | 951 | 951 | 1559 | 1559 | 951 | 951
[5 empty] | 5 | 6 | 2425 | 2430 | 1480 | 1481 | 2431 | 2433 | 1481 | 1482 |  | FCA or AICtk |  |  |  | Isck |  | AIC Tk
[5 empty] | 6 | 4 | 3806 | 3825 | 2345 | 2350 | 3830 | 3837 | 2351 | 2353 |  | #DIV/0! |  |  |  | 0 |  | 0
[5 empty] | 7 | 3 | 4760 | 4802 | 2948 | 2958 | 4760 | 4802 | 2948 | 2958
[5 empty] | 8 | 2 | 5906 | 6044 | 3713 | 3729 | 5989 | 6087 | 3733 | 3739 | [5 empty] | KVA
[5 empty] | 9 | 1 | 7292 | 7493 | 4645 | 4678 | 7454 | 7579 | 4686 | 4699 | [5 empty] | 0
[5 empty] | 10 | 1/0 | 8924 | 9317 | 5777 | 5838 | 9209 | 9472 | 5852 | 5879
[5 empty] | 11 | 2/0 | 10755 | 11423 | 7186 | 7301 | 11244 | 11703 | 7327 | 7372 | [5 empty] | %Z
[5 empty] | 12 | 3/0 | 12843 | 13923 | 8826 | 9110 | 13656 | 14410 | 9077 | 9242 | [5 empty] | 0
[5 empty] | 13 | 4/0 | 15082 | 16673 | 10740 | 11174 | 16391 | 17482 | 11184 | 11408
[5 empty] | 14 | 250 | 16483 | 18593 | 12122 | 12862 | 18310 | 19779 | 12796 | 13236
[5 empty] | 15 | 300 | 18176 | 20867 | 13909 | 14922 | 20617 | 22524 | 14916 | 15494
[5 empty] | 16 | 350 | 19703 | 22736 | 15484 | 16812 | 19557 | 22736 | 15413 | 16812
[5 empty] | 17 | 400 | 20565 | 24296 | 16670 | 18505 | 24253 | 26915 | 18461 | 19587
[5 empty] | 18 | 500 | 22185 | 26706 | 18755 | 21390 | 26980 | 30028 | 21394 | 22987
[5 empty] | 19 | 600 | 22965 | 28033 | 20093 | 23451 | 28752 | 32236 | 23633 | 25750
[5 empty] | 20 | 750 | 24136 | 28303 | 21766 | 23491 | 31050 | 32404 | 26431 | 25682
[5 empty] | 21 | 1000 | 25278 | 31490 | 23477 | 28778 | 33864 | 37197 | 29864 | 32938
[5 empty] | 1 | 480 | 7 | 3
[5 empty] | 2 | 208 | 8 | 5
[5 empty] | 3 |  | 9 | 7
[5 empty] | 4 |  | 10 | 9
[5 empty] | 5 |  | 11 | 4
[5 empty] | 6 |  | 12 | 6
[5 empty] | 7 |  | 13 | 8
[5 empty] | 8 |  | 14 | 10

## Selective Coordination Tool
Selective Coordination Tool
Selectively Coordinated Breakers |  |  | Voltage
| Circuit Breaker Type | Coordinates To (A) | Available Fault Currents
BRANCH |  |  | LP
DP
CB3 |  |  | MDP
LP (from Generator)
CB2 |  |  |  |  | 11 | 3
|  |  |  | branch / cb3, cb2 / branch | 1 | 1
cb2 / cb 1
CB1 |  |  | Generator Fault Current | cb 1 / main | 10 | 2
|  | 625 | Gen Fault Current (A) |  | 12 | 4
MAIN |  |  | Generator kW |  | 13 | 5
Output Voltage (V,3Ø)
|  |  | X'' d (per Unit) * |  | 14 | 6
GEN |  | 625
* (see Application Notes)
[5 empty] | 15 | 7
G
MAIN
ATS
CB1
CB2
CB3
BRANCH
GEN
DP
LP
MDP

## Fault Current Application Hints
Application Hints
Fault Current Calculator
Sum the horsepowers of all motors on system (optional but recommended)
Provide AIC if the transformer is inside your system, or if the utility available
current is known
Enter the primary voltage to the transformer if available (used only of you
have provided a value for the available primary fault current)
Remember, enter in kVA (i.e. enter 1 MVA as 1000)
Input the impedance as a percentage, not a decimal (i.e. 5.5% would be 5.5).
This is the rated secondary based on the transformer and voltage you supplied.
If you have the actual available fault current, either as given to you from the utility, or if you are using this program to calculate fault currents at other parts of the system where the AIC is known, input the number here. It will automatically override the transformer based information.
The conductor length is one way - don't forget changes in elevation (from panel to ceiling, etc.).
Notes on Printing
When printing the Calculator page, go to File/Print Setup and select "black& white" under Print options.

## Selective Coordination Info
Important Information on Selective Coordination
What is Selective Coordination
Selective Coordination is a design requirement newly added by both the 2005 and 2008 National Electrical Code® to Article 700 - Emergency Systems (see 700.27), Article 701 - Legally Required Standby Systems (see 701.18), and by the 2008 NEC to Article 708 - Critical Operations Power Systems (see 708.54). These Articles also apply to Health Care Facilities as noted in 517.26. Prior to 2005, Selective Coordination was only required for some elevator applications by Article 620. For sections of systems falling under Articles 700 , 701 and 708, the Engineer is responsible for selecting overcurrent devices such that only the device directly upstream of the fault will trip. This differs from traditional typical coordination and coordination studies that attempted to minimize the chance of nuisance trips where a fault may open more than one device.
To design a Selectively Coordinated system, the Engineer must choose pairs of overcurrent devices whose time current curves do no overlap in either the thermal range or the instantaneous range up to the current available at the downstream breaker. Example: A 20A branch breaker feeding egress lighting per 2005 NEC® 700 must selectively coordinate with all upstream devices. The 20A breaker is in a branch panel that has 2500A of available fault current. To selectively coordinate, only the 20A breaker may trip under this fault - this means that the next upstream device must not trip with 2500A of current prior to the 20A device opening. The smallest device with an instantaneous trip that will not operate at 2500A (including the tolerance band) is a 400A thermal magnetic or a 300A solid state circuit breaker. That second breaker must in turn coordinate with the next upstream device at the fault current level available at that second breaker, and so on, up to and including the service entrance overcurrent device. When the system is being powered by the emergency source, the coordination must now be calculated based on the new available fault currents, in most cases sourced from an emergency generator.
The Siemens Selective Coordination Tool will identify commonly used Siemens circuit breakers whose trip curves do not overlap for the conditions selected by the Engineer. The Tool will identify coordinated commonly used breaker pairs for up to five levels of distribution. In some cases, Siemens has additional devices and solutions available for especially difficult design conditions - please feel free to contact your local Siemens Consultant Account Manager for additional assistance and options. The Siemens Selective Coordination Tool is based on data for Siemens circuit breakers that may or may not be similar to products by other manufacturers. We suggest noting on the panel schedule the Siemens breaker suggested by the Tool and calling for an equivalent product for other approved manufacturers. Inclusion of the Siemens breaker type and size will provide some of the information needed to select the alternate product.
The choice of selectively coordinated devices requires calculation (and frequently recalculation) by the engineer of the available fault currents at various points in the system, and often requires resizing panels, switchboards, conductors, conduits and other system components - this redesign can not be done during the bidding process, and can be extremely costly if done during construction. For this reason, the Engineer is responsible for selecting and calling for the correct selectively coordinated devices - please let us know if Siemens can assist you!
How to Use The Selective Coordination Tool
This summary page and the hints page are not intended to provide a complete technical discussion of the issue or comprehensive instructions for the Tool's use - if additional information or assistance is needed, please contact your local Siemens Consultant Account Manager. For more information, click on the "Sel. Coord. Tool Hints" tab below. Thanks for specifying Siemens!
Disclaimer - Please Read
This spreadsheet and worksheet is intended to provide technical and basic design information for the user. Siemens Energy & Automation, Inc. reserves the right, without notice, to change information or data originally in this spreadsheet and to discontinue or limit its distribution. The data and information presented in this spreadsheet is believed to be accurate. However, any and all liability for the content, or any omissions from this program, including any inaccuracies, errors, or misstatements in such data, calculations or information, is expressly disclaimed. The software, data, calculation results and other information are provided without warranty of any kind, either express or implied, including but not limited to, the implied warranties of merchantability, or fitness for a particular purpose. Siemens Energy & Automation, Inc. disclaims any liability related to the use of this program, software, calculations or other information.

## Sel Coord Tool Hints
Siemens Selective Coordination Tool Hints
This is a generic one-line that can be used for many different configurations. The labels "MDP", "DP" and "LP" are to identify three available fault current locations ("LP" must always be given because there will always be a branch device with an available fault current). For assistance or more information, contact your Siemens Consultant Account Manager.
This Tool identifies breaker pairs that coordinate to a given available fault current (AFC). To meet the requirements of Selective Coordination, BRANCH and CB3 must coordinate to the AFC at "LP", CB3 and CB2 must coordinate to the AFC at LP, CB2 and CB1 must coordinate to the AFC at DP, and CB1 and MAIN must coordinate to the AFC at MDP (the downstream device determines the level of coordination). For example, if you only have a 20A branch (BRANCH) in a MLO panel ("LP") fed from a feeder breaker (CB1) in "MDP", you may select "none" for CB3 and CB2. BRANCH will then coordinate with CB1 to the AFC at "LP", and CB1 will coordinate with MAIN to the AFC at "MDP".
Provide the voltage for the breakers being evaluated - use 240 for a 208V system.
Determine the available fault currents for the applicable locations. Remember, you will have to recalculate available fault currents and recheck the breaker pairs each time you increase the conductor size. The Fault Current Calculator makes this easy.
You will need to find the subtransient impedance (X''d) for your generator from the generator manufacturer - this must be a per unit value.
This section calculates the AFC at the generator. You can use the Fault Current Calculator to quickly determine the available fault current at "LP" - just insert the Gen Fault Current answer into the "or Secondary Available Fault Current" field and solve for the proper distance and conductor.
Always pull down the list to see your choices - sometimes the smallest is not displayed first.
You may not always have a breaker that corresponds to CB1, CB2 or CB3. If that is the case, select "none" from the available breaker pulldown list.
The "Coordinates To" field indicates the highest level of fault current (in amps) to which the shown breaker pair will selectively coordinate.
Only the white fields are user inputs.
The breakers shown are the type, not the specific breaker. Example: FD 250 indicates a type FD breaker with a 250A trip. This breaker type is available in four AIC rating models, the FD6 (65/35kAIC at 240/480V), the HFD6 (100/65kAIC), the HHFD6 (200/100kAIC), and the CFD6 (200/200kAIC) - refer to the SpeedFax for the correct specific breaker. Make sure you specify the correct version or required AIC level in the specifications or by schedule.
An "s" designation after the breaker type (ex. "SMD 800 s") indicates a solid state electronic trip circuit breaker. No "s" indicates a thermal-magnetic trip circuit breaker. ALL type WL are solid state.
The "UL 489" and "UL 1066" notations for the type WL insulated case breaker indicate switchboard application or switchgear application, respectively. The "FS" notation indicates the frame size.

## 480V Selectively Coord. Pairs (hidden)
480V Selectively Coordinated Pairs |  |  |  | 240
480
| Column1 |  | Column1 |  | Column1
| BQD 20 | 625 | BQD 100 |  | BQD 20 | None |  | None |  | None |  | BQD 100 | 625 | BQD 100 | 625
| BQD 20 | 590 | ED 60 |  | BQD 100 | BQD 100 | 625 | BQD 100 | 625 | BQD 100 | 625 | ED 60 | 590 | ED 60 | 590
| BQD 20 | 880 | ED 100 |  | ED 60 | ED 60 | 590 | ED 60 | 590 | ED 60 | 590 | ED 100 | 880 | ED 100 | 880
| BQD 20 | 1000 | ED 125 |  | ED 100 | ED 100 | 880 | ED 100 | 880 | ED 100 | 880 | ED 125 | 1000 | ED 125 | 1000
| BQD 20 | 960 | FD 100 |  | ED 125 | ED 125 | 1000 | ED 125 | 1000 | ED 125 | 1000 | FD 100 | 960 | FD 100 | 960
| BQD 20 | 1200 | FD 150 |  | FD 100 | FD 100 | 960 | FD 100 | 960 | FD 100 | 960 | FD 150 | 1200 | FD 150 | 1200
| BQD 20 | 1600 | FD 200 |  | FD 150 | FD 150 | 1200 | FD 150 | 1200 | FD 150 | 1200 | FD 200 | 1600 | FD 200 | 1600
| BQD 20 | 1950 | FD 250 |  | FD 200 | FD 200 | 1600 | FD 200 | 1600 | FD 200 | 1600 | FD 250 | 1950 | FD 250 | 1950
| BQD 20 | 1950 | JD 300 |  | FD 250 | FD 250 | 1950 | FD 250 | 1950 | FD 250 | 1950 | JD 300 | 1950 | JD 300 | 1950
| BQD 20 | 3200 | JD 400 |  | JD 300 | JD 300 | 1950 | JD 300 | 1950 | JD 300 | 1950 | JD 400 | 3200 | JD 400 | 3200
| BQD 20 | 2000 | SJD 200 s |  | JD 400 | JD 400 | 3200 | JD 400 | 3200 | JD 400 | 3200 | SJD 200 s | 2000 | SJD 200 s | 2000
| BQD 20 | 3100 | SJD 300 s |  | SJD 200 s | SJD 200 s | 2000 | SJD 200 s | 2000 | SJD 200 s | 2000 | SJD 300 s | 3100 | SJD 300 s | 3100
| BQD 20 | 4200 | SJD 400 s |  | SJD 300 s | SJD 300 s | 3100 | SJD 300 s | 3100 | SJD 300 s | 3100 | SJD 400 s | 4200 | SJD 400 s | 4200
| BQD 20 | 1980 | LD 250 |  | SJD 400 s | SJD 400 s | 4200 | SJD 400 s | 4200 | SJD 400 s | 4200 | LD 250 | 1980 | LD 250 | 1980
| BQD 20 | 3200 | LD 400 |  | LD 250 | LD 250 | 1980 | LD 250 | 1980 | LD 250 | 1980 | LD 400 | 3200 | LD 400 | 3200
| BQD 20 | 4800 | LD 500 |  | LD 400 | LD 400 | 3200 | LD 400 | 3200 | LD 400 | 3200 | LD 500 | 4800 | LD 500 | 4800
| BQD 20 | 4800 | LD 600 |  | LD 500 | LD 500 | 4800 | LD 500 | 4800 | LD 500 | 4800 | LD 600 | 4800 | LD 600 | 4800
| BQD 20 | 3100 | SLD 300 s |  | LD 600 | LD 600 | 4800 | LD 600 | 4800 | LD 600 | 4800 | SLD 300 s | 3100 | SLD 300 s | 3100
| BQD 20 | 4100 | SLD 400 s |  | SLD 300 s | SLD 300 s | 3100 | SLD 300 s | 3100 | SLD 300 s | 3100 | SLD 400 s | 4100 | SLD 400 s | 4100
| BQD 20 | 5200 | SLD 500 s |  | SLD 400 s | SLD 400 s | 4100 | SLD 400 s | 4100 | SLD 400 s | 4100 | SLD 500 s | 5200 | SLD 500 s | 5200
| BQD 20 | 6200 | SLD 600 s |  | SLD 500 s | SLD 500 s | 5200 | SLD 500 s | 5200 | SLD 500 s | 5200 | SLD 600 s | 6200 | SLD 600 s | 6200
| BQD 20 | 5000 | MD 500 |  | SLD 600 s | SLD 600 s | 6200 | SLD 600 s | 6200 | SLD 600 s | 6200 | MD 500 | 5000 | MD 500 | 5000
| BQD 20 | 6500 | MD 600 |  | MD 500 | MD 500 | 5000 | MD 500 | 5000 | MD 500 | 5000 | MD 600 | 6500 | MD 600 | 6500
| BQD 20 | 6500 | MD 800 |  | MD 600 | MD 600 | 6500 | MD 600 | 6500 | MD 600 | 6500 | MD 800 | 6500 | MD 800 | 6500
| BQD 20 | 4800 | MG 600 |  | MD 800 | MD 800 | 6500 | MD 800 | 6500 | MD 800 | 6500 | MG 600 | 4800 | MG 600 | 4800
| BQD 20 | 5200 | MG 800 |  | MG 600 | MG 600 | 4800 | MG 600 | 4800 | MG 600 | 4800 | MG 800 | 5200 | MG 800 | 5200
| BQD 20 | 7200 | SMD 600 s |  | MG 800 | MG 800 | 5200 | MG 800 | 5200 | MG 800 | 5200 | SMD 600 s | 7200 | SMD 600 s | 7200
| BQD 20 | 9600 | SMD 800 s |  | SMD 600 s | SMD 600 s | 7200 | SMD 600 s | 7200 | SMD 600 s | 7200 | SMD 800 s | 9600 | SMD 800 s | 9600
| BQD 20 | 4800 | MG 600 s |  | SMD 800 s | SMD 800 s | 9600 | SMD 800 s | 9600 | SMD 800 s | 9600 | MG 600 s | 4800 | MG 600 s | 4800
| BQD 20 | 4800 | MG 800 s |  | MG 600 s | MG 600 s | 4800 | MG 600 s | 4800 | MG 600 s | 4800 | MG 800 s | 4800 | MG 800 s | 4800
| BQD 20 | 8000 | ND 1000 |  | MG 800 s | MG 800 s | 4800 | MG 800 s | 4800 | MG 800 s | 4800 | ND 1000 | 8000 | ND 1000 | 8000
| BQD 20 | 8000 | ND 1200 |  | ND 1000 | ND 1000 | 8000 | ND 1000 | 8000 | ND 1000 | 8000 | ND 1200 | 8000 | ND 1200 | 8000
| BQD 20 | 6400 | NG 800 |  | ND 1200 | ND 1200 | 8000 | ND 1200 | 8000 | ND 1200 | 8000 | NG 800 | 6400 | NG 800 | 6400
| BQD 20 | 8000 | NG 1000 |  | NG 800 | NG 800 | 6400 | NG 800 | 6400 | NG 800 | 6400 | NG 1000 | 8000 | NG 1000 | 8000
| BQD 20 | 9600 | NG 1200 |  | NG 1000 | NG 1000 | 8000 | NG 1000 | 8000 | NG 1000 | 8000 | NG 1200 | 9600 | NG 1200 | 9600
| BQD 20 | 9400 | SND 800 s |  | NG 1200 | NG 1200 | 9600 | NG 1200 | 9600 | NG 1200 | 9600 | SND 800 s | 9400 | SND 800 s | 9400
| BQD 20 | 10000 | SND 1000 s |  | SND 800 s | SND 800 s | 9400 | SND 800 s | 9400 | SND 800 s | 9400 | SND 1000 s | 10000 | SND 1000 s | 10000
| BQD 20 | 10000 | SND 1200 s |  | SND 1000 s | SND 1000 s | 10000 | SND 1000 s | 10000 | SND 1000 s | 10000 | SND 1200 s | 10000 | SND 1200 s | 10000
| BQD 20 | 7040 | NG 800 s |  | SND 1200 s | SND 1200 s | 10000 | SND 1200 s | 10000 | SND 1200 s | 10000 | NG 800 s | 7040 | NG 800 s | 7040
| BQD 20 | 8800 | NG 1000 s |  | NG 800 s | NG 800 s | 7040 | NG 800 s | 7040 | NG 800 s | 7040 | NG 1000 s | 8800 | NG 1000 s | 8800
| BQD 20 | 9600 | NG 1200 s |  | NG 1000 s | NG 1000 s | 8800 | NG 1000 s | 8800 | NG 1000 s | 8800 | NG 1200 s | 9600 | NG 1200 s | 9600
| BQD 20 | 8000 | PD 1200 |  | NG 1200 s | NG 1200 s | 9600 | NG 1200 s | 9600 | NG 1200 s | 9600 | PD 1200 | 8000 | PD 1200 | 8000
| BQD 20 | 8000 | PD 1600 |  | PD 1200 | PD 1200 | 8000 | PD 1200 | 8000 | PD 1200 | 8000 | PD 1600 | 8000 | PD 1600 | 8000
| BQD 20 | 9600 | PG 1200 |  | PD 1600 | PD 1600 | 8000 | PD 1600 | 8000 | PD 1600 | 8000 | PG 1200 | 9600 | PG 1200 | 9600
| BQD 20 | 9600 | PG 1600 |  | PG 1200 | PG 1200 | 9600 | PG 1200 | 9600 | PG 1200 | 9600 | PG 1600 | 9600 | PG 1600 | 9600
| BQD 20 | 10000 | SPD 1400 s |  | PG 1600 | PG 1600 | 9600 | PG 1600 | 9600 | PG 1600 | 9600 | SPD 1400 s | 10000 | SPD 1400 s | 10000
| BQD 20 | 10000 | SPD 1600 s |  | SPD 1400 s | SPD 1400 s | 10000 | SPD 1400 s | 10000 | SPD 1400 s | 10000 | SPD 1600 s | 10000 | SPD 1600 s | 10000
| BQD 20 | 9600 | PG 1200 s |  | SPD 1600 s | SPD 1600 s | 10000 | SPD 1600 s | 10000 | SPD 1600 s | 10000 | PG 1200 s | 9600 | PG 1200 s | 9600
| BQD 20 | 7680 | PG 1600 s |  | PG 1200 s | PG 1200 s | 9600 | PG 1200 s | 9600 | PG 1200 s | 9600 | PG 1600 s | 7680 | PG 1600 s | 7680
| BQD 20 | 14000 | WL 800 FS1 UL489 |  | PG 1600 s | PG 1600 s | 7680 | PG 1600 s | 7680 | PG 1600 s | 7680 | WL 800 FS1 UL489 | 14000 | WL 800 FS1 UL489 | 14000
| BQD 20 | 14000 | WL 1200 FS1 UL489 |  | WL 800 FS1 UL489 | WL 800 FS1 UL489 | 14000 | WL 800 FS1 UL489 | 14000 | WL 800 FS1 UL489 | 14000 | WL 1200 FS1 UL489 | 14000 | WL 1200 FS1 UL489 | 14000
| BQD 20 | 14000 | WL 800 FS2 UL489 |  | WL 1200 FS1 UL489 | WL 1200 FS1 UL489 | 14000 | WL 1200 FS1 UL489 | 14000 | WL 1200 FS1 UL489 | 14000 | WL 800 FS2 UL489 | 14000 | WL 800 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 1200 FS2 UL489 |  | WL 800 FS2 UL489 | WL 800 FS2 UL489 | 14000 | WL 800 FS2 UL489 | 14000 | WL 800 FS2 UL489 | 14000 | WL 1200 FS2 UL489 | 14000 | WL 1200 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 1600 FS2 UL489 |  | WL 1200 FS2 UL489 | WL 1200 FS2 UL489 | 14000 | WL 1200 FS2 UL489 | 14000 | WL 1200 FS2 UL489 | 14000 | WL 1600 FS2 UL489 | 14000 | WL 1600 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 2000 FS2 UL489 |  | WL 1600 FS2 UL489 | WL 1600 FS2 UL489 | 14000 | WL 1600 FS2 UL489 | 14000 | WL 1600 FS2 UL489 | 14000 | WL 2000 FS2 UL489 | 14000 | WL 2000 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 2500 FS2 UL489 |  | WL 2000 FS2 UL489 | WL 2000 FS2 UL489 | 14000 | WL 2000 FS2 UL489 | 14000 | WL 2000 FS2 UL489 | 14000 | WL 2500 FS2 UL489 | 14000 | WL 2500 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 3000 FS2 UL489 |  | WL 2500 FS2 UL489 | WL 2500 FS2 UL489 | 14000 | WL 2500 FS2 UL489 | 14000 | WL 2500 FS2 UL489 | 14000 | WL 3000 FS2 UL489 | 14000 | WL 3000 FS2 UL489 | 14000
| BQD 20 | 14000 | WL 4000 FS3 UL489 |  | WL 3000 FS2 UL489 | WL 3000 FS2 UL489 | 14000 | WL 3000 FS2 UL489 | 14000 | WL 3000 FS2 UL489 | 14000 | WL 4000 FS3 UL489 | 14000 | WL 4000 FS3 UL489 | 14000
| BQD 20 | 14000 | WL 5000 FS3 UL489 |  | WL 4000 FS3 UL489 | WL 4000 FS3 UL489 | 14000 | WL 4000 FS3 UL489 | 14000 | WL 4000 FS3 UL489 | 14000 | WL 5000 FS3 UL489 | 14000 | WL 5000 FS3 UL489 | 14000
| BQD 20 | 14000 | WL 800 N FS2 UL1066 |  | WL 5000 FS3 UL489 | WL 5000 FS3 UL489 | 14000 | WL 5000 FS3 UL489 | 14000 | WL 5000 FS3 UL489 | 14000 | WL 800 N FS2 UL1066 | 14000 | WL 800 N FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 800 S,H FS2 UL1066 |  | WL 800 N FS2 UL1066 | WL 800 N FS2 UL1066 | 14000 | WL 800 N FS2 UL1066 | 14000 | WL 800 N FS2 UL1066 | 14000 | WL 800 S,H FS2 UL1066 | 14000 | WL 800 S,H FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 800 L FS2 UL1066 |  | WL 800 S,H FS2 UL1066 | WL 800 S,H FS2 UL1066 | 14000 | WL 800 S,H FS2 UL1066 | 14000 | WL 800 S,H FS2 UL1066 | 14000 | WL 800 L FS2 UL1066 | 14000 | WL 800 L FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 800 F FS2 UL1066 |  | WL 800 L FS2 UL1066 | WL 800 L FS2 UL1066 | 14000 | WL 800 L FS2 UL1066 | 14000 | WL 800 L FS2 UL1066 | 14000 | WL 800 F FS2 UL1066 | 14000 | WL 800 F FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 1600 N FS2 UL1066 |  | WL 800 F FS2 UL1066 | WL 800 F FS2 UL1066 | 14000 | WL 800 F FS2 UL1066 | 14000 | WL 800 F FS2 UL1066 | 14000 | WL 1600 N FS2 UL1066 | 14000 | WL 1600 N FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 1600 S,H FS2 UL1066 |  | WL 1600 N FS2 UL1066 | WL 1600 N FS2 UL1066 | 14000 | WL 1600 N FS2 UL1066 | 14000 | WL 1600 N FS2 UL1066 | 14000 | WL 1600 S,H FS2 UL1066 | 14000 | WL 1600 S,H FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 1600 L FS2 UL1066 |  | WL 1600 S,H FS2 UL1066 | WL 1600 S,H FS2 UL1066 | 14000 | WL 1600 S,H FS2 UL1066 | 14000 | WL 1600 S,H FS2 UL1066 | 14000 | WL 1600 L FS2 UL1066 | 14000 | WL 1600 L FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 1600 F FS2 UL1066 |  | WL 1600 L FS2 UL1066 | WL 1600 L FS2 UL1066 | 14000 | WL 1600 L FS2 UL1066 | 14000 | WL 1600 L FS2 UL1066 | 14000 | WL 1600 F FS2 UL1066 | 14000 | WL 1600 F FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 2000 S,H FS2 UL1066 |  | WL 1600 F FS2 UL1066 | WL 1600 F FS2 UL1066 | 14000 | WL 1600 F FS2 UL1066 | 14000 | WL 1600 F FS2 UL1066 | 14000 | WL 2000 S,H FS2 UL1066 | 14000 | WL 2000 S,H FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 2000 L FS2 UL1066 |  | WL 2000 S,H FS2 UL1066 | WL 2000 S,H FS2 UL1066 | 14000 | WL 2000 S,H FS2 UL1066 | 14000 | WL 2000 S,H FS2 UL1066 | 14000 | WL 2000 L FS2 UL1066 | 14000 | WL 2000 L FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 2000 F FS2 UL1066 |  | WL 2000 L FS2 UL1066 | WL 2000 L FS2 UL1066 | 14000 | WL 2000 L FS2 UL1066 | 14000 | WL 2000 L FS2 UL1066 | 14000 | WL 2000 F FS2 UL1066 | 14000 | WL 2000 F FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 3200 S,H FS2 UL1066 |  | WL 2000 F FS2 UL1066 | WL 2000 F FS2 UL1066 | 14000 | WL 2000 F FS2 UL1066 | 14000 | WL 2000 F FS2 UL1066 | 14000 | WL 3200 S,H FS2 UL1066 | 14000 | WL 3200 S,H FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 3200 L FS2 UL1066 |  | WL 3200 S,H FS2 UL1066 | WL 3200 S,H FS2 UL1066 | 14000 | WL 3200 S,H FS2 UL1066 | 14000 | WL 3200 S,H FS2 UL1066 | 14000 | WL 3200 L FS2 UL1066 | 14000 | WL 3200 L FS2 UL1066 | 14000
| BQD 20 | 14000 | WL 3200 M FS3 UL1066 |  | WL 3200 L FS2 UL1066 | WL 3200 L FS2 UL1066 | 14000 | WL 3200 L FS2 UL1066 | 14000 | WL 3200 L FS2 UL1066 | 14000 | WL 3200 M FS3 UL1066 | 14000 | WL 3200 M FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 3200 F FS3 UL1066 |  | WL 3200 M FS3 UL1066 | WL 3200 M FS3 UL1066 | 14000 | WL 3200 M FS3 UL1066 | 14000 | WL 3200 M FS3 UL1066 | 14000 | WL 3200 F FS3 UL1066 | 14000 | WL 3200 F FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 4000 H FS3 UL1066 |  | WL 3200 F FS3 UL1066 | WL 3200 F FS3 UL1066 | 14000 | WL 3200 F FS3 UL1066 | 14000 | WL 3200 F FS3 UL1066 | 14000 | WL 4000 H FS3 UL1066 | 14000 | WL 4000 H FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 4000 L,M FS3 UL1066 |  | WL 4000 H FS3 UL1066 | WL 4000 H FS3 UL1066 | 14000 | WL 4000 H FS3 UL1066 | 14000 | WL 4000 H FS3 UL1066 | 14000 | WL 4000 L,M FS3 UL1066 | 14000 | WL 4000 L,M FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 4000 F FS3 UL1066 |  | WL 4000 L,M FS3 UL1066 | WL 4000 L,M FS3 UL1066 | 14000 | WL 4000 L,M FS3 UL1066 | 14000 | WL 4000 L,M FS3 UL1066 | 14000 | WL 4000 F FS3 UL1066 | 14000 | WL 4000 F FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 5000 H FS3 UL1066 |  | WL 4000 F FS3 UL1066 | WL 4000 F FS3 UL1066 | 14000 | WL 4000 F FS3 UL1066 | 14000 | WL 4000 F FS3 UL1066 | 14000 | WL 5000 H FS3 UL1066 | 14000 | WL 5000 H FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 5000 L,M FS3 UL1066 |  | WL 5000 H FS3 UL1066 | WL 5000 H FS3 UL1066 | 14000 | WL 5000 H FS3 UL1066 | 14000 | WL 5000 H FS3 UL1066 | 14000 | WL 5000 L,M FS3 UL1066 | 14000 | WL 5000 L,M FS3 UL1066 | 14000
| BQD 20 | 14000 | WL 5000 F FS3 UL1066 |  | WL 5000 L,M FS3 UL1066 | WL 5000 L,M FS3 UL1066 | 14000 | WL 5000 L,M FS3 UL1066 | 14000 | WL 5000 L,M FS3 UL1066 | 14000 | WL 5000 F FS3 UL1066 | 14000 | WL 5000 F FS3 UL1066 | 14000
| BQD 100 | 1200 | FD 150 |  | WL 5000 F FS3 UL1066 | WL 5000 F FS3 UL1066 | 14000 | WL 5000 F FS3 UL1066 | 14000 | WL 5000 F FS3 UL1066 | 14000
| BQD 100 | 1600 | FD 200
| BQD 100 | 1950 | FD 250
| BQD 100 | 1950 | JD 300
| BQD 100 | 3200 | JD 400
| BQD 100 | 2000 | SJD 200 s
| BQD 100 | 3100 | SJD 300 s
| BQD 100 | 4200 | SJD 400 s
| BQD 100 | 1980 | LD 250
| BQD 100 | 3200 | LD 400
| BQD 100 | 4800 | LD 500
| BQD 100 | 4800 | LD 600
| BQD 100 | 3100 | SLD 300 s
| BQD 100 | 4100 | SLD 400 s
| BQD 100 | 5200 | SLD 500 s
| BQD 100 | 6200 | SLD 600 s
| BQD 100 | 5000 | MD 500
| BQD 100 | 6500 | MD 600
| BQD 100 | 6500 | MD 800
| BQD 100 | 4800 | MG 600
| BQD 100 | 5200 | MG 800
| BQD 100 | 7200 | SMD 600 s
| BQD 100 | 9600 | SMD 800 s
| BQD 100 | 4800 | MG 600 s
| BQD 100 | 4800 | MG 800 s
| BQD 100 | 8000 | ND 1000
| BQD 100 | 8000 | ND 1200
| BQD 100 | 6400 | NG 800
| BQD 100 | 8000 | NG 1000
| BQD 100 | 9600 | NG 1200
| BQD 100 | 9400 | SND 800 s
| BQD 100 | 10000 | SND 1000 s
| BQD 100 | 10000 | SND 1200 s
| BQD 100 | 7040 | NG 800 s
| BQD 100 | 8800 | NG 1000 s
| BQD 100 | 9600 | NG 1200 s
| BQD 100 | 8000 | PD 1200
| BQD 100 | 8000 | PD 1600
| BQD 100 | 9600 | PG 1200
| BQD 100 | 9600 | PG 1600
| BQD 100 | 10000 | SPD 1400 s
| BQD 100 | 10000 | SPD 1600 s
| BQD 100 | 9600 | PG 1200 s
| BQD 100 | 7680 | PG 1600 s
| BQD 100 | 14000 | WL 800 FS1 UL489
| BQD 100 | 14000 | WL 1200 FS1 UL489
| BQD 100 | 14000 | WL 800 FS2 UL489
| BQD 100 | 14000 | WL 1200 FS2 UL489
| BQD 100 | 14000 | WL 1600 FS2 UL489
| BQD 100 | 14000 | WL 2000 FS2 UL489
| BQD 100 | 14000 | WL 2500 FS2 UL489
| BQD 100 | 14000 | WL 3000 FS2 UL489
| BQD 100 | 14000 | WL 4000 FS3 UL489
| BQD 100 | 14000 | WL 5000 FS3 UL489
| BQD 100 | 14000 | WL 800 N FS2 UL1066
| BQD 100 | 14000 | WL 800 S,H FS2 UL1066
| BQD 100 | 14000 | WL 800 L FS2 UL1066
| BQD 100 | 14000 | WL 800 F FS2 UL1066
| BQD 100 | 14000 | WL 1600 N FS2 UL1066
| BQD 100 | 14000 | WL 1600 S,H FS2 UL1066
| BQD 100 | 14000 | WL 1600 L FS2 UL1066
| BQD 100 | 14000 | WL 1600 F FS2 UL1066
| BQD 100 | 14000 | WL 2000 S,H FS2 UL1066
| BQD 100 | 14000 | WL 2000 L FS2 UL1066
| BQD 100 | 14000 | WL 2000 F FS2 UL1066
| BQD 100 | 14000 | WL 3200 S,H FS2 UL1066
| BQD 100 | 14000 | WL 3200 L FS2 UL1066
| BQD 100 | 14000 | WL 3200 M FS3 UL1066
| BQD 100 | 14000 | WL 3200 F FS3 UL1066
| BQD 100 | 14000 | WL 4000 H FS3 UL1066
| BQD 100 | 14000 | WL 4000 L,M FS3 UL1066
| BQD 100 | 14000 | WL 4000 F FS3 UL1066
| BQD 100 | 14000 | WL 5000 H FS3 UL1066
| BQD 100 | 14000 | WL 5000 L,M FS3 UL1066
| BQD 100 | 14000 | WL 5000 F FS3 UL1066
| ED 60 | 960 | FD 100
| ED 60 | 1200 | FD 150
| ED 60 | 1600 | FD 200
| ED 60 | 1950 | FD 250
| ED 60 | 1950 | JD 300
| ED 60 | 3200 | JD 400
| ED 60 | 2000 | SJD 200 s
| ED 60 | 3100 | SJD 300 s
| ED 60 | 4200 | SJD 400 s
| ED 60 | 1980 | LD 250
| ED 60 | 3200 | LD 400
| ED 60 | 4800 | LD 500
| ED 60 | 4800 | LD 600
| ED 60 | 3100 | SLD 300 s
| ED 60 | 4100 | SLD 400 s
| ED 60 | 5200 | SLD 500 s
| ED 60 | 6200 | SLD 600 s
| ED 60 | 5000 | MD 500
| ED 60 | 6500 | MD 600
| ED 60 | 6500 | MD 800
| ED 60 | 4800 | MG 600
| ED 60 | 5200 | MG 800
| ED 60 | 7200 | SMD 600 s
| ED 60 | 9600 | SMD 800 s
| ED 60 | 4800 | MG 600 s
| ED 60 | 4800 | MG 800 s
| ED 60 | 8000 | ND 1000
| ED 60 | 8000 | ND 1200
| ED 60 | 6400 | NG 800
| ED 60 | 8000 | NG 1000
| ED 60 | 9600 | NG 1200
| ED 60 | 9400 | SND 800 s
| ED 60 | 10000 | SND 1000 s
| ED 60 | 10000 | SND 1200 s
| ED 60 | 7040 | NG 800 s
| ED 60 | 8800 | NG 1000 s
| ED 60 | 9600 | NG 1200 s
| ED 60 | 8000 | PD 1200
| ED 60 | 8000 | PD 1600
| ED 60 | 9600 | PG 1200
| ED 60 | 9600 | PG 1600
| ED 60 | 10000 | SPD 1400 s
| ED 60 | 10000 | SPD 1600 s
| ED 60 | 9600 | PG 1200 s
| ED 60 | 7680 | PG 1600 s
| ED 60 | 52000 | WL 800 FS1 UL489
| ED 60 | 52000 | WL 1200 FS1 UL489
| ED 60 | 52000 | WL 800 FS2 UL489
| ED 60 | 52000 | WL 1200 FS2 UL489
| ED 60 | 52000 | WL 1600 FS2 UL489
| ED 60 | 52000 | WL 2000 FS2 UL489
| ED 60 | 52000 | WL 2500 FS2 UL489
| ED 60 | 52000 | WL 3000 FS2 UL489
| ED 60 | 68000 | WL 4000 FS3 UL489
| ED 60 | 68000 | WL 5000 FS3 UL489
| ED 60 | 50000 | WL 800 N FS2 UL1066
| ED 60 | 65000 | WL 800 S,H FS2 UL1066
| ED 60 | 85000 | WL 800 L FS2 UL1066
| ED 60 | 20000 | WL 800 F FS2 UL1066
| ED 60 | 50000 | WL 1600 N FS2 UL1066
| ED 60 | 65000 | WL 1600 S,H FS2 UL1066
| ED 60 | 85000 | WL 1600 L FS2 UL1066
| ED 60 | 20000 | WL 1600 F FS2 UL1066
| ED 60 | 65000 | WL 2000 S,H FS2 UL1066
| ED 60 | 85000 | WL 2000 L FS2 UL1066
| ED 60 | 20000 | WL 2000 F FS2 UL1066
| ED 60 | 65000 | WL 3200 S,H FS2 UL1066
| ED 60 | 85000 | WL 3200 L FS2 UL1066
| ED 60 | 100000 | WL 3200 M FS3 UL1066
| ED 60 | 40000 | WL 3200 F FS3 UL1066
| ED 60 | 85000 | WL 4000 H FS3 UL1066
| ED 60 | 100000 | WL 4000 L,M FS3 UL1066
| ED 60 | 40000 | WL 4000 F FS3 UL1066
| ED 60 | 85000 | WL 5000 H FS3 UL1066
| ED 60 | 100000 | WL 5000 L,M FS3 UL1066
| ED 60 | 40000 | WL 5000 F FS3 UL1066
| ED 100 | 1200 | FD 150
| ED 100 | 1600 | FD 200
| ED 100 | 1950 | FD 250
| ED 100 | 1950 | JD 300
| ED 100 | 3200 | JD 400
| ED 100 | 2000 | SJD 200 s
| ED 100 | 3100 | SJD 300 s
| ED 100 | 4200 | SJD 400 s
| ED 100 | 1980 | LD 250
| ED 100 | 3200 | LD 400
| ED 100 | 4800 | LD 500
| ED 100 | 4800 | LD 600
| ED 100 | 3100 | SLD 300 s
| ED 100 | 4100 | SLD 400 s
| ED 100 | 5200 | SLD 500 s
| ED 100 | 6200 | SLD 600 s
| ED 100 | 5000 | MD 500
| ED 100 | 6500 | MD 600
| ED 100 | 6500 | MD 800
| ED 100 | 4800 | MG 600
| ED 100 | 5200 | MG 800
| ED 100 | 7200 | SMD 600 s
| ED 100 | 9600 | SMD 800 s
| ED 100 | 4800 | MG 600 s
| ED 100 | 4800 | MG 800 s
| ED 100 | 8000 | ND 1000
| ED 100 | 8000 | ND 1200
| ED 100 | 6400 | NG 800
| ED 100 | 8000 | NG 1000
| ED 100 | 9600 | NG 1200
| ED 100 | 9400 | SND 800 s
| ED 100 | 10000 | SND 1000 s
| ED 100 | 10000 | SND 1200 s
| ED 100 | 7040 | NG 800 s
| ED 100 | 8800 | NG 1000 s
| ED 100 | 9600 | NG 1200 s
| ED 100 | 8000 | PD 1200
| ED 100 | 8000 | PD 1600
| ED 100 | 9600 | PG 1200
| ED 100 | 9600 | PG 1600
| ED 100 | 10000 | SPD 1400 s
| ED 100 | 10000 | SPD 1600 s
| ED 100 | 9600 | PG 1200 s
| ED 100 | 7680 | PG 1600 s
| ED 100 | 52000 | WL 800 FS1 UL489
| ED 100 | 52000 | WL 1200 FS1 UL489
| ED 100 | 52000 | WL 800 FS2 UL489
| ED 100 | 52000 | WL 1200 FS2 UL489
| ED 100 | 52000 | WL 1600 FS2 UL489
| ED 100 | 52000 | WL 2000 FS2 UL489
| ED 100 | 52000 | WL 2500 FS2 UL489
| ED 100 | 52000 | WL 3000 FS2 UL489
| ED 100 | 68000 | WL 4000 FS3 UL489
| ED 100 | 68000 | WL 5000 FS3 UL489
| ED 100 | 50000 | WL 800 N FS2 UL1066
| ED 100 | 65000 | WL 800 S,H FS2 UL1066
| ED 100 | 85000 | WL 800 L FS2 UL1066
| ED 100 | 20000 | WL 800 F FS2 UL1066
| ED 100 | 50000 | WL 1600 N FS2 UL1066
| ED 100 | 65000 | WL 1600 S,H FS2 UL1066
| ED 100 | 85000 | WL 1600 L FS2 UL1066
| ED 100 | 20000 | WL 1600 F FS2 UL1066
| ED 100 | 65000 | WL 2000 S,H FS2 UL1066
| ED 100 | 85000 | WL 2000 L FS2 UL1066
| ED 100 | 20000 | WL 2000 F FS2 UL1066
| ED 100 | 65000 | WL 3200 S,H FS2 UL1066
| ED 100 | 85000 | WL 3200 L FS2 UL1066
| ED 100 | 100000 | WL 3200 M FS3 UL1066
| ED 100 | 40000 | WL 3200 F FS3 UL1066
| ED 100 | 85000 | WL 4000 H FS3 UL1066
| ED 100 | 100000 | WL 4000 L,M FS3 UL1066
| ED 100 | 40000 | WL 4000 F FS3 UL1066
| ED 100 | 85000 | WL 5000 H FS3 UL1066
| ED 100 | 100000 | WL 5000 L,M FS3 UL1066
| ED 100 | 40000 | WL 5000 F FS3 UL1066
| ED 125 | 1600 | FD 200
| ED 125 | 1950 | FD 250
| ED 125 | 1950 | JD 300
| ED 125 | 3200 | JD 400
| ED 125 | 2000 | SJD 200 s
| ED 125 | 3100 | SJD 300 s
| ED 125 | 4200 | SJD 400 s
| ED 125 | 1980 | LD 250
| ED 125 | 3200 | LD 400
| ED 125 | 4800 | LD 500
| ED 125 | 4800 | LD 600
| ED 125 | 3100 | SLD 300 s
| ED 125 | 4100 | SLD 400 s
| ED 125 | 5200 | SLD 500 s
| ED 125 | 6200 | SLD 600 s
| ED 125 | 5000 | MD 500
| ED 125 | 6500 | MD 600
| ED 125 | 6500 | MD 800
| ED 125 | 4800 | MG 600
| ED 125 | 5200 | MG 800
| ED 125 | 7200 | SMD 600 s
| ED 125 | 9600 | SMD 800 s
| ED 125 | 4800 | MG 600 s
| ED 125 | 4800 | MG 800 s
| ED 125 | 8000 | ND 1000
| ED 125 | 8000 | ND 1200
| ED 125 | 6400 | NG 800
| ED 125 | 8000 | NG 1000
| ED 125 | 9600 | NG 1200
| ED 125 | 9400 | SND 800 s
| ED 125 | 10000 | SND 1000 s
| ED 125 | 10000 | SND 1200 s
| ED 125 | 7040 | NG 800 s
| ED 125 | 8800 | NG 1000 s
| ED 125 | 9600 | NG 1200 s
| ED 125 | 8000 | PD 1200
| ED 125 | 8000 | PD 1600
| ED 125 | 9600 | PG 1200
| ED 125 | 9600 | PG 1600
| ED 125 | 10000 | SPD 1400 s
| ED 125 | 10000 | SPD 1600 s
| ED 125 | 9600 | PG 1200 s
| ED 125 | 7680 | PG 1600 s
| ED 125 | 52000 | WL 800 FS1 UL489
| ED 125 | 52000 | WL 1200 FS1 UL489
| ED 125 | 52000 | WL 800 FS2 UL489
| ED 125 | 52000 | WL 1200 FS2 UL489
| ED 125 | 52000 | WL 1600 FS2 UL489
| ED 125 | 52000 | WL 2000 FS2 UL489
| ED 125 | 52000 | WL 2500 FS2 UL489
| ED 125 | 52000 | WL 3000 FS2 UL489
| ED 125 | 68000 | WL 4000 FS3 UL489
| ED 125 | 68000 | WL 5000 FS3 UL489
| ED 125 | 50000 | WL 800 N FS2 UL1066
| ED 125 | 65000 | WL 800 S,H FS2 UL1066
| ED 125 | 85000 | WL 800 L FS2 UL1066
| ED 125 | 20000 | WL 800 F FS2 UL1066
| ED 125 | 50000 | WL 1600 N FS2 UL1066
| ED 125 | 65000 | WL 1600 S,H FS2 UL1066
| ED 125 | 85000 | WL 1600 L FS2 UL1066
| ED 125 | 20000 | WL 1600 F FS2 UL1066
| ED 125 | 65000 | WL 2000 S,H FS2 UL1066
| ED 125 | 85000 | WL 2000 L FS2 UL1066
| ED 125 | 20000 | WL 2000 F FS2 UL1066
| ED 125 | 65000 | WL 3200 S,H FS2 UL1066
| ED 125 | 85000 | WL 3200 L FS2 UL1066
| ED 125 | 100000 | WL 3200 M FS3 UL1066
| ED 125 | 40000 | WL 3200 F FS3 UL1066
| ED 125 | 85000 | WL 4000 H FS3 UL1066
| ED 125 | 100000 | WL 4000 L,M FS3 UL1066
| ED 125 | 40000 | WL 4000 F FS3 UL1066
| ED 125 | 85000 | WL 5000 H FS3 UL1066
| ED 125 | 100000 | WL 5000 L,M FS3 UL1066
| ED 125 | 40000 | WL 5000 F FS3 UL1066
| FD 100 | 1600 | FD 200
| FD 100 | 1950 | FD 250
| FD 100 | 1950 | JD 300
| FD 100 | 3200 | JD 400
| FD 100 | 2000 | SJD 200 s
| FD 100 | 3100 | SJD 300 s
| FD 100 | 4200 | SJD 400 s
| FD 100 | 1980 | LD 250
| FD 100 | 3200 | LD 400
| FD 100 | 4800 | LD 500
| FD 100 | 4800 | LD 600
| FD 100 | 3100 | SLD 300 s
| FD 100 | 4100 | SLD 400 s
| FD 100 | 5200 | SLD 500 s
| FD 100 | 6200 | SLD 600 s
| FD 100 | 5000 | MD 500
| FD 100 | 6500 | MD 600
| FD 100 | 6500 | MD 800
| FD 100 | 4800 | MG 600
| FD 100 | 5200 | MG 800
| FD 100 | 7200 | SMD 600 s
| FD 100 | 9600 | SMD 800 s
| FD 100 | 4800 | MG 600 s
| FD 100 | 4800 | MG 800 s
| FD 100 | 8000 | ND 1000
| FD 100 | 8000 | ND 1200
| FD 100 | 6400 | NG 800
| FD 100 | 8000 | NG 1000
| FD 100 | 9600 | NG 1200
| FD 100 | 9400 | SND 800 s
| FD 100 | 10000 | SND 1000 s
| FD 100 | 10000 | SND 1200 s
| FD 100 | 7040 | NG 800 s
| FD 100 | 8800 | NG 1000 s
| FD 100 | 9600 | NG 1200 s
| FD 100 | 8000 | PD 1200
| FD 100 | 8000 | PD 1600
| FD 100 | 9600 | PG 1200
| FD 100 | 9600 | PG 1600
| FD 100 | 10000 | SPD 1400 s
| FD 100 | 10000 | SPD 1600 s
| FD 100 | 9600 | PG 1200 s
| FD 100 | 7680 | PG 1600 s
| FD 100 | 52000 | WL 800 FS1 UL489
| FD 100 | 52000 | WL 1200 FS1 UL489
| FD 100 | 52000 | WL 800 FS2 UL489
| FD 100 | 52000 | WL 1200 FS2 UL489
| FD 100 | 52000 | WL 1600 FS2 UL489
| FD 100 | 52000 | WL 2000 FS2 UL489
| FD 100 | 52000 | WL 2500 FS2 UL489
| FD 100 | 52000 | WL 3000 FS2 UL489
| FD 100 | 68000 | WL 4000 FS3 UL489
| FD 100 | 68000 | WL 5000 FS3 UL489
| FD 100 | 50000 | WL 800 N FS2 UL1066
| FD 100 | 65000 | WL 800 S,H FS2 UL1066
| FD 100 | 85000 | WL 800 L FS2 UL1066
| FD 100 | 20000 | WL 800 F FS2 UL1066
| FD 100 | 50000 | WL 1600 N FS2 UL1066
| FD 100 | 65000 | WL 1600 S,H FS2 UL1066
| FD 100 | 85000 | WL 1600 L FS2 UL1066
| FD 100 | 20000 | WL 1600 F FS2 UL1066
| FD 100 | 65000 | WL 2000 S,H FS2 UL1066
| FD 100 | 85000 | WL 2000 L FS2 UL1066
| FD 100 | 20000 | WL 2000 F FS2 UL1066
| FD 100 | 65000 | WL 3200 S,H FS2 UL1066
| FD 100 | 85000 | WL 3200 L FS2 UL1066
| FD 100 | 100000 | WL 3200 M FS3 UL1066
| FD 100 | 40000 | WL 3200 F FS3 UL1066
| FD 100 | 85000 | WL 4000 H FS3 UL1066
| FD 100 | 100000 | WL 4000 L,M FS3 UL1066
| FD 100 | 40000 | WL 4000 F FS3 UL1066
| FD 100 | 85000 | WL 5000 H FS3 UL1066
| FD 100 | 100000 | WL 5000 L,M FS3 UL1066
| FD 100 | 40000 | WL 5000 F FS3 UL1066
| FD 150 | 1950 | JD 300
| FD 150 | 3200 | JD 400
| FD 150 | 3100 | SJD 300 s
| FD 150 | 4200 | SJD 400 s
| FD 150 | 3200 | LD 400
| FD 150 | 4800 | LD 500
| FD 150 | 4800 | LD 600
| FD 150 | 3100 | SLD 300 s
| FD 150 | 4100 | SLD 400 s
| FD 150 | 5200 | SLD 500 s
| FD 150 | 6200 | SLD 600 s
| FD 150 | 5000 | MD 500
| FD 150 | 6500 | MD 600
| FD 150 | 6500 | MD 800
| FD 150 | 4800 | MG 600
| FD 150 | 5200 | MG 800
| FD 150 | 7200 | SMD 600 s
| FD 150 | 9600 | SMD 800 s
| FD 150 | 4800 | MG 600 s
| FD 150 | 4800 | MG 800 s
| FD 150 | 8000 | ND 1000
| FD 150 | 8000 | ND 1200
| FD 150 | 6400 | NG 800
| FD 150 | 8000 | NG 1000
| FD 150 | 9600 | NG 1200
| FD 150 | 9400 | SND 800 s
| FD 150 | 10000 | SND 1000 s
| FD 150 | 10000 | SND 1200 s
| FD 150 | 7040 | NG 800 s
| FD 150 | 8800 | NG 1000 s
| FD 150 | 9600 | NG 1200 s
| FD 150 | 8000 | PD 1200
| FD 150 | 8000 | PD 1600
| FD 150 | 9600 | PG 1200
| FD 150 | 9600 | PG 1600
| FD 150 | 10000 | SPD 1400 s
| FD 150 | 10000 | SPD 1600 s
| FD 150 | 9600 | PG 1200 s
| FD 150 | 7680 | PG 1600 s
| FD 150 | 52000 | WL 800 FS1 UL489
| FD 150 | 52000 | WL 1200 FS1 UL489
| FD 150 | 52000 | WL 800 FS2 UL489
| FD 150 | 52000 | WL 1200 FS2 UL489
| FD 150 | 52000 | WL 1600 FS2 UL489
| FD 150 | 52000 | WL 2000 FS2 UL489
| FD 150 | 52000 | WL 2500 FS2 UL489
| FD 150 | 52000 | WL 3000 FS2 UL489
| FD 150 | 68000 | WL 4000 FS3 UL489
| FD 150 | 68000 | WL 5000 FS3 UL489
| FD 150 | 50000 | WL 800 N FS2 UL1066
| FD 150 | 65000 | WL 800 S,H FS2 UL1066
| FD 150 | 85000 | WL 800 L FS2 UL1066
| FD 150 | 20000 | WL 800 F FS2 UL1066
| FD 150 | 50000 | WL 1600 N FS2 UL1066
| FD 150 | 65000 | WL 1600 S,H FS2 UL1066
| FD 150 | 85000 | WL 1600 L FS2 UL1066
| FD 150 | 20000 | WL 1600 F FS2 UL1066
| FD 150 | 65000 | WL 2000 S,H FS2 UL1066
| FD 150 | 85000 | WL 2000 L FS2 UL1066
| FD 150 | 20000 | WL 2000 F FS2 UL1066
| FD 150 | 65000 | WL 3200 S,H FS2 UL1066
| FD 150 | 85000 | WL 3200 L FS2 UL1066
| FD 150 | 100000 | WL 3200 M FS3 UL1066
| FD 150 | 40000 | WL 3200 F FS3 UL1066
| FD 150 | 85000 | WL 4000 H FS3 UL1066
| FD 150 | 100000 | WL 4000 L,M FS3 UL1066
| FD 150 | 40000 | WL 4000 F FS3 UL1066
| FD 150 | 85000 | WL 5000 H FS3 UL1066
| FD 150 | 100000 | WL 5000 L,M FS3 UL1066
| FD 150 | 40000 | WL 5000 F FS3 UL1066
| FD 200 | 3200 | JD 400
| FD 200 | 4200 | SJD 400 s
| FD 200 | 3200 | LD 400
| FD 200 | 4800 | LD 500
| FD 200 | 4800 | LD 600
| FD 200 | 4100 | SLD 400 s
| FD 200 | 5200 | SLD 500 s
| FD 200 | 6200 | SLD 600 s
| FD 200 | 5000 | MD 500
| FD 200 | 6500 | MD 600
| FD 200 | 6500 | MD 800
| FD 200 | 4800 | MG 600
| FD 200 | 5200 | MG 800
| FD 200 | 7200 | SMD 600 s
| FD 200 | 9600 | SMD 800 s
| FD 200 | 4800 | MG 600 s
| FD 200 | 4800 | MG 800 s
| FD 200 | 8000 | ND 1000
| FD 200 | 8000 | ND 1200
| FD 200 | 6400 | NG 800
| FD 200 | 8000 | NG 1000
| FD 200 | 9600 | NG 1200
| FD 200 | 9400 | SND 800 s
| FD 200 | 10000 | SND 1000 s
| FD 200 | 10000 | SND 1200 s
| FD 200 | 7040 | NG 800 s
| FD 200 | 8800 | NG 1000 s
| FD 200 | 9600 | NG 1200 s
| FD 200 | 8000 | PD 1200
| FD 200 | 8000 | PD 1600
| FD 200 | 9600 | PG 1200
| FD 200 | 9600 | PG 1600
| FD 200 | 10000 | SPD 1400 s
| FD 200 | 10000 | SPD 1600 s
| FD 200 | 9600 | PG 1200 s
| FD 200 | 7680 | PG 1600 s
| FD 200 | 52000 | WL 800 FS1 UL489
| FD 200 | 52000 | WL 1200 FS1 UL489
| FD 200 | 52000 | WL 800 FS2 UL489
| FD 200 | 52000 | WL 1200 FS2 UL489
| FD 200 | 52000 | WL 1600 FS2 UL489
| FD 200 | 52000 | WL 2000 FS2 UL489
| FD 200 | 52000 | WL 2500 FS2 UL489
| FD 200 | 52000 | WL 3000 FS2 UL489
| FD 200 | 68000 | WL 4000 FS3 UL489
| FD 200 | 68000 | WL 5000 FS3 UL489
| FD 200 | 50000 | WL 800 N FS2 UL1066
| FD 200 | 65000 | WL 800 S,H FS2 UL1066
| FD 200 | 85000 | WL 800 L FS2 UL1066
| FD 200 | 20000 | WL 800 F FS2 UL1066
| FD 200 | 50000 | WL 1600 N FS2 UL1066
| FD 200 | 65000 | WL 1600 S,H FS2 UL1066
| FD 200 | 85000 | WL 1600 L FS2 UL1066
| FD 200 | 20000 | WL 1600 F FS2 UL1066
| FD 200 | 65000 | WL 2000 S,H FS2 UL1066
| FD 200 | 85000 | WL 2000 L FS2 UL1066
| FD 200 | 20000 | WL 2000 F FS2 UL1066
| FD 200 | 65000 | WL 3200 S,H FS2 UL1066
| FD 200 | 85000 | WL 3200 L FS2 UL1066
| FD 200 | 100000 | WL 3200 M FS3 UL1066
| FD 200 | 40000 | WL 3200 F FS3 UL1066
| FD 200 | 85000 | WL 4000 H FS3 UL1066
| FD 200 | 100000 | WL 4000 L,M FS3 UL1066
| FD 200 | 40000 | WL 4000 F FS3 UL1066
| FD 200 | 85000 | WL 5000 H FS3 UL1066
| FD 200 | 100000 | WL 5000 L,M FS3 UL1066
| FD 200 | 40000 | WL 5000 F FS3 UL1066
| FD 250 | 4800 | LD 500
| FD 250 | 4800 | LD 600
| FD 250 | 5200 | SLD 500 s
| FD 250 | 6200 | SLD 600 s
| FD 250 | 5000 | MD 500
| FD 250 | 6500 | MD 600
| FD 250 | 6500 | MD 800
| FD 250 | 4800 | MG 600
| FD 250 | 5200 | MG 800
| FD 250 | 7200 | SMD 600 s
| FD 250 | 9600 | SMD 800 s
| FD 250 | 4800 | MG 600 s
| FD 250 | 4800 | MG 800 s
| FD 250 | 8000 | ND 1000
| FD 250 | 8000 | ND 1200
| FD 250 | 6400 | NG 800
| FD 250 | 8000 | NG 1000
| FD 250 | 9600 | NG 1200
| FD 250 | 9400 | SND 800 s
| FD 250 | 10000 | SND 1000 s
| FD 250 | 10000 | SND 1200 s
| FD 250 | 7040 | NG 800 s
| FD 250 | 8800 | NG 1000 s
| FD 250 | 9600 | NG 1200 s
| FD 250 | 8000 | PD 1200
| FD 250 | 8000 | PD 1600
| FD 250 | 9600 | PG 1200
| FD 250 | 9600 | PG 1600
| FD 250 | 10000 | SPD 1400 s
| FD 250 | 10000 | SPD 1600 s
| FD 250 | 9600 | PG 1200 s
| FD 250 | 7680 | PG 1600 s
| FD 250 | 52000 | WL 800 FS1 UL489
| FD 250 | 52000 | WL 1200 FS1 UL489
| FD 250 | 52000 | WL 800 FS2 UL489
| FD 250 | 52000 | WL 1200 FS2 UL489
| FD 250 | 52000 | WL 1600 FS2 UL489
| FD 250 | 52000 | WL 2000 FS2 UL489
| FD 250 | 52000 | WL 2500 FS2 UL489
| FD 250 | 52000 | WL 3000 FS2 UL489
| FD 250 | 68000 | WL 4000 FS3 UL489
| FD 250 | 68000 | WL 5000 FS3 UL489
| FD 250 | 50000 | WL 800 N FS2 UL1066
| FD 250 | 65000 | WL 800 S,H FS2 UL1066
| FD 250 | 85000 | WL 800 L FS2 UL1066
| FD 250 | 20000 | WL 800 F FS2 UL1066
| FD 250 | 50000 | WL 1600 N FS2 UL1066
| FD 250 | 65000 | WL 1600 S,H FS2 UL1066
| FD 250 | 85000 | WL 1600 L FS2 UL1066
| FD 250 | 20000 | WL 1600 F FS2 UL1066
| FD 250 | 65000 | WL 2000 S,H FS2 UL1066
| FD 250 | 85000 | WL 2000 L FS2 UL1066
| FD 250 | 20000 | WL 2000 F FS2 UL1066
| FD 250 | 65000 | WL 3200 S,H FS2 UL1066
| FD 250 | 85000 | WL 3200 L FS2 UL1066
| FD 250 | 100000 | WL 3200 M FS3 UL1066
| FD 250 | 40000 | WL 3200 F FS3 UL1066
| FD 250 | 85000 | WL 4000 H FS3 UL1066
| FD 250 | 100000 | WL 4000 L,M FS3 UL1066
| FD 250 | 40000 | WL 4000 F FS3 UL1066
| FD 250 | 85000 | WL 5000 H FS3 UL1066
| FD 250 | 100000 | WL 5000 L,M FS3 UL1066
| FD 250 | 40000 | WL 5000 F FS3 UL1066
| JD 300 | 4800 | LD 600
| JD 300 | 6200 | SLD 600 s
| JD 300 | 6500 | MD 600
| JD 300 | 6500 | MD 800
| JD 300 | 4800 | MG 600
| JD 300 | 5200 | MG 800
| JD 300 | 7200 | SMD 600 s
| JD 300 | 9600 | SMD 800 s
| JD 300 | 4800 | MG 800 s
| JD 300 | 8000 | ND 1000
| JD 300 | 8000 | ND 1200
| JD 300 | 6400 | NG 800
| JD 300 | 8000 | NG 1000
| JD 300 | 9600 | NG 1200
| JD 300 | 9400 | SND 800 s
| JD 300 | 10000 | SND 1000 s
| JD 300 | 10000 | SND 1200 s
| JD 300 | 7040 | NG 800 s
| JD 300 | 8800 | NG 1000 s
| JD 300 | 9600 | NG 1200 s
| JD 300 | 8000 | PD 1200
| JD 300 | 8000 | PD 1600
| JD 300 | 9600 | PG 1200
| JD 300 | 9600 | PG 1600
| JD 300 | 10000 | SPD 1400 s
| JD 300 | 10000 | SPD 1600 s
| JD 300 | 9600 | PG 1200 s
| JD 300 | 7680 | PG 1600 s
| JD 300 | 52000 | WL 800 FS1 UL489
| JD 300 | 52000 | WL 1200 FS1 UL489
| JD 300 | 52000 | WL 800 FS2 UL489
| JD 300 | 52000 | WL 1200 FS2 UL489
| JD 300 | 52000 | WL 1600 FS2 UL489
| JD 300 | 52000 | WL 2000 FS2 UL489
| JD 300 | 52000 | WL 2500 FS2 UL489
| JD 300 | 52000 | WL 3000 FS2 UL489
| JD 300 | 68000 | WL 4000 FS3 UL489
| JD 300 | 68000 | WL 5000 FS3 UL489
| JD 300 | 50000 | WL 800 N FS2 UL1066
| JD 300 | 65000 | WL 800 S,H FS2 UL1066
| JD 300 | 85000 | WL 800 L FS2 UL1066
| JD 300 | 20000 | WL 800 F FS2 UL1066
| JD 300 | 50000 | WL 1600 N FS2 UL1066
| JD 300 | 65000 | WL 1600 S,H FS2 UL1066
| JD 300 | 85000 | WL 1600 L FS2 UL1066
| JD 300 | 20000 | WL 1600 F FS2 UL1066
| JD 300 | 65000 | WL 2000 S,H FS2 UL1066
| JD 300 | 85000 | WL 2000 L FS2 UL1066
| JD 300 | 20000 | WL 2000 F FS2 UL1066
| JD 300 | 65000 | WL 3200 S,H FS2 UL1066
| JD 300 | 85000 | WL 3200 L FS2 UL1066
| JD 300 | 100000 | WL 3200 M FS3 UL1066
| JD 300 | 40000 | WL 3200 F FS3 UL1066
| JD 300 | 85000 | WL 4000 H FS3 UL1066
| JD 300 | 100000 | WL 4000 L,M FS3 UL1066
| JD 300 | 40000 | WL 4000 F FS3 UL1066
| JD 300 | 85000 | WL 5000 H FS3 UL1066
| JD 300 | 100000 | WL 5000 L,M FS3 UL1066
| JD 300 | 40000 | WL 5000 F FS3 UL1066
| JD 400 | 6500 | MD 800
| JD 400 | 5200 | MG 800
| JD 400 | 9600 | SMD 800 s
| JD 400 | 4800 | MG 800 s
| JD 400 | 8000 | ND 1000
| JD 400 | 8000 | ND 1200
| JD 400 | 6400 | NG 800
| JD 400 | 8000 | NG 1000
| JD 400 | 9600 | NG 1200
| JD 400 | 9400 | SND 800 s
| JD 400 | 10000 | SND 1000 s
| JD 400 | 10000 | SND 1200 s
| JD 400 | 7040 | NG 800 s
| JD 400 | 8800 | NG 1000 s
| JD 400 | 9600 | NG 1200 s
| JD 400 | 8000 | PD 1200
| JD 400 | 8000 | PD 1600
| JD 400 | 9600 | PG 1200
| JD 400 | 9600 | PG 1600
| JD 400 | 10000 | SPD 1400 s
| JD 400 | 10000 | SPD 1600 s
| JD 400 | 9600 | PG 1200 s
| JD 400 | 7680 | PG 1600 s
| JD 400 | 52000 | WL 800 FS1 UL489
| JD 400 | 52000 | WL 1200 FS1 UL489
| JD 400 | 52000 | WL 800 FS2 UL489
| JD 400 | 52000 | WL 1200 FS2 UL489
| JD 400 | 52000 | WL 1600 FS2 UL489
| JD 400 | 52000 | WL 2000 FS2 UL489
| JD 400 | 52000 | WL 2500 FS2 UL489
| JD 400 | 52000 | WL 3000 FS2 UL489
| JD 400 | 68000 | WL 4000 FS3 UL489
| JD 400 | 68000 | WL 5000 FS3 UL489
| JD 400 | 50000 | WL 800 N FS2 UL1066
| JD 400 | 65000 | WL 800 S,H FS2 UL1066
| JD 400 | 85000 | WL 800 L FS2 UL1066
| JD 400 | 20000 | WL 800 F FS2 UL1066
| JD 400 | 50000 | WL 1600 N FS2 UL1066
| JD 400 | 65000 | WL 1600 S,H FS2 UL1066
| JD 400 | 85000 | WL 1600 L FS2 UL1066
| JD 400 | 20000 | WL 1600 F FS2 UL1066
| JD 400 | 65000 | WL 2000 S,H FS2 UL1066
| JD 400 | 85000 | WL 2000 L FS2 UL1066
| JD 400 | 20000 | WL 2000 F FS2 UL1066
| JD 400 | 65000 | WL 3200 S,H FS2 UL1066
| JD 400 | 85000 | WL 3200 L FS2 UL1066
| JD 400 | 100000 | WL 3200 M FS3 UL1066
| JD 400 | 40000 | WL 3200 F FS3 UL1066
| JD 400 | 85000 | WL 4000 H FS3 UL1066
| JD 400 | 100000 | WL 4000 L,M FS3 UL1066
| JD 400 | 40000 | WL 4000 F FS3 UL1066
| JD 400 | 85000 | WL 5000 H FS3 UL1066
| JD 400 | 100000 | WL 5000 L,M FS3 UL1066
| JD 400 | 40000 | WL 5000 F FS3 UL1066
| SJD 200 s | 3200 | JD 400
| SJD 200 s | 4200 | SJD 400 s
| SJD 200 s | 3200 | LD 400
| SJD 200 s | 4800 | LD 500
| SJD 200 s | 4800 | LD 600
| SJD 200 s | 4100 | SLD 400 s
| SJD 200 s | 5200 | SLD 500 s
| SJD 200 s | 6200 | SLD 600 s
| SJD 200 s | 5000 | MD 500
| SJD 200 s | 6500 | MD 600
| SJD 200 s | 6500 | MD 800
| SJD 200 s | 4800 | MG 600
| SJD 200 s | 5200 | MG 800
| SJD 200 s | 7200 | SMD 600 s
| SJD 200 s | 9600 | SMD 800 s
| SJD 200 s | 4800 | MG 600 s
| SJD 200 s | 4800 | MG 800 s
| SJD 200 s | 8000 | ND 1000
| SJD 200 s | 8000 | ND 1200
| SJD 200 s | 6400 | NG 800
| SJD 200 s | 8000 | NG 1000
| SJD 200 s | 9600 | NG 1200
| SJD 200 s | 9400 | SND 800 s
| SJD 200 s | 10000 | SND 1000 s
| SJD 200 s | 10000 | SND 1200 s
| SJD 200 s | 7040 | NG 800 s
| SJD 200 s | 8800 | NG 1000 s
| SJD 200 s | 9600 | NG 1200 s
| SJD 200 s | 8000 | PD 1200
| SJD 200 s | 8000 | PD 1600
| SJD 200 s | 9600 | PG 1200
| SJD 200 s | 9600 | PG 1600
| SJD 200 s | 10000 | SPD 1400 s
| SJD 200 s | 10000 | SPD 1600 s
| SJD 200 s | 9600 | PG 1200 s
| SJD 200 s | 7680 | PG 1600 s
| SJD 200 s | 52000 | WL 800 FS1 UL489
| SJD 200 s | 52000 | WL 1200 FS1 UL489
| SJD 200 s | 52000 | WL 800 FS2 UL489
| SJD 200 s | 52000 | WL 1200 FS2 UL489
| SJD 200 s | 52000 | WL 1600 FS2 UL489
| SJD 200 s | 52000 | WL 2000 FS2 UL489
| SJD 200 s | 52000 | WL 2500 FS2 UL489
| SJD 200 s | 52000 | WL 3000 FS2 UL489
| SJD 200 s | 68000 | WL 4000 FS3 UL489
| SJD 200 s | 68000 | WL 5000 FS3 UL489
| SJD 200 s | 50000 | WL 800 N FS2 UL1066
| SJD 200 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 800 L FS2 UL1066
| SJD 200 s | 20000 | WL 800 F FS2 UL1066
| SJD 200 s | 50000 | WL 1600 N FS2 UL1066
| SJD 200 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 1600 L FS2 UL1066
| SJD 200 s | 20000 | WL 1600 F FS2 UL1066
| SJD 200 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 2000 L FS2 UL1066
| SJD 200 s | 20000 | WL 2000 F FS2 UL1066
| SJD 200 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 3200 L FS2 UL1066
| SJD 200 s | 100000 | WL 3200 M FS3 UL1066
| SJD 200 s | 40000 | WL 3200 F FS3 UL1066
| SJD 200 s | 85000 | WL 4000 H FS3 UL1066
| SJD 200 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 200 s | 40000 | WL 4000 F FS3 UL1066
| SJD 200 s | 85000 | WL 5000 H FS3 UL1066
| SJD 200 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 200 s | 40000 | WL 5000 F FS3 UL1066
| SJD 300 s | 4800 | LD 600
| SJD 300 s | 6200 | SLD 600 s
| SJD 300 s | 6500 | MD 600
| SJD 300 s | 6500 | MD 800
| SJD 300 s | 4800 | MG 600
| SJD 300 s | 5200 | MG 800
| SJD 300 s | 7200 | SMD 600 s
| SJD 300 s | 9600 | SMD 800 s
| SJD 300 s | 4800 | MG 800 s
| SJD 300 s | 8000 | ND 1000
| SJD 300 s | 8000 | ND 1200
| SJD 300 s | 6400 | NG 800
| SJD 300 s | 8000 | NG 1000
| SJD 300 s | 9600 | NG 1200
| SJD 300 s | 9400 | SND 800 s
| SJD 300 s | 10000 | SND 1000 s
| SJD 300 s | 10000 | SND 1200 s
| SJD 300 s | 7040 | NG 800 s
| SJD 300 s | 8800 | NG 1000 s
| SJD 300 s | 9600 | NG 1200 s
| SJD 300 s | 8000 | PD 1200
| SJD 300 s | 8000 | PD 1600
| SJD 300 s | 9600 | PG 1200
| SJD 300 s | 9600 | PG 1600
| SJD 300 s | 10000 | SPD 1400 s
| SJD 300 s | 10000 | SPD 1600 s
| SJD 300 s | 9600 | PG 1200 s
| SJD 300 s | 7680 | PG 1600 s
| SJD 300 s | 52000 | WL 800 FS1 UL489
| SJD 300 s | 52000 | WL 1200 FS1 UL489
| SJD 300 s | 52000 | WL 800 FS2 UL489
| SJD 300 s | 52000 | WL 1200 FS2 UL489
| SJD 300 s | 52000 | WL 1600 FS2 UL489
| SJD 300 s | 52000 | WL 2000 FS2 UL489
| SJD 300 s | 52000 | WL 2500 FS2 UL489
| SJD 300 s | 52000 | WL 3000 FS2 UL489
| SJD 300 s | 68000 | WL 4000 FS3 UL489
| SJD 300 s | 68000 | WL 5000 FS3 UL489
| SJD 300 s | 50000 | WL 800 N FS2 UL1066
| SJD 300 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 800 L FS2 UL1066
| SJD 300 s | 20000 | WL 800 F FS2 UL1066
| SJD 300 s | 50000 | WL 1600 N FS2 UL1066
| SJD 300 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 1600 L FS2 UL1066
| SJD 300 s | 20000 | WL 1600 F FS2 UL1066
| SJD 300 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 2000 L FS2 UL1066
| SJD 300 s | 20000 | WL 2000 F FS2 UL1066
| SJD 300 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 3200 L FS2 UL1066
| SJD 300 s | 100000 | WL 3200 M FS3 UL1066
| SJD 300 s | 40000 | WL 3200 F FS3 UL1066
| SJD 300 s | 85000 | WL 4000 H FS3 UL1066
| SJD 300 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 300 s | 40000 | WL 4000 F FS3 UL1066
| SJD 300 s | 85000 | WL 5000 H FS3 UL1066
| SJD 300 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 300 s | 40000 | WL 5000 F FS3 UL1066
| SJD 400 s | 6500 | MD 800
| SJD 400 s | 5200 | MG 800
| SJD 400 s | 9600 | SMD 800 s
| SJD 400 s | 4800 | MG 800 s
| SJD 400 s | 8000 | ND 1000
| SJD 400 s | 8000 | ND 1200
| SJD 400 s | 6400 | NG 800
| SJD 400 s | 8000 | NG 1000
| SJD 400 s | 9600 | NG 1200
| SJD 400 s | 9400 | SND 800 s
| SJD 400 s | 10000 | SND 1000 s
| SJD 400 s | 10000 | SND 1200 s
| SJD 400 s | 7040 | NG 800 s
| SJD 400 s | 8800 | NG 1000 s
| SJD 400 s | 9600 | NG 1200 s
| SJD 400 s | 8000 | PD 1200
| SJD 400 s | 8000 | PD 1600
| SJD 400 s | 9600 | PG 1200
| SJD 400 s | 9600 | PG 1600
| SJD 400 s | 10000 | SPD 1400 s
| SJD 400 s | 10000 | SPD 1600 s
| SJD 400 s | 9600 | PG 1200 s
| SJD 400 s | 7680 | PG 1600 s
| SJD 400 s | 52000 | WL 800 FS1 UL489
| SJD 400 s | 52000 | WL 1200 FS1 UL489
| SJD 400 s | 52000 | WL 800 FS2 UL489
| SJD 400 s | 52000 | WL 1200 FS2 UL489
| SJD 400 s | 52000 | WL 1600 FS2 UL489
| SJD 400 s | 52000 | WL 2000 FS2 UL489
| SJD 400 s | 52000 | WL 2500 FS2 UL489
| SJD 400 s | 52000 | WL 3000 FS2 UL489
| SJD 400 s | 68000 | WL 4000 FS3 UL489
| SJD 400 s | 68000 | WL 5000 FS3 UL489
| SJD 400 s | 50000 | WL 800 N FS2 UL1066
| SJD 400 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 800 L FS2 UL1066
| SJD 400 s | 20000 | WL 800 F FS2 UL1066
| SJD 400 s | 50000 | WL 1600 N FS2 UL1066
| SJD 400 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 1600 L FS2 UL1066
| SJD 400 s | 20000 | WL 1600 F FS2 UL1066
| SJD 400 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 2000 L FS2 UL1066
| SJD 400 s | 20000 | WL 2000 F FS2 UL1066
| SJD 400 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 3200 L FS2 UL1066
| SJD 400 s | 100000 | WL 3200 M FS3 UL1066
| SJD 400 s | 40000 | WL 3200 F FS3 UL1066
| SJD 400 s | 85000 | WL 4000 H FS3 UL1066
| SJD 400 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 400 s | 40000 | WL 4000 F FS3 UL1066
| SJD 400 s | 85000 | WL 5000 H FS3 UL1066
| SJD 400 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 400 s | 40000 | WL 5000 F FS3 UL1066
| LD 250 | 4800 | LD 600
| LD 250 | 5200 | SLD 500 s
| LD 250 | 6200 | SLD 600 s
| LD 250 | 5000 | MD 500
| LD 250 | 6500 | MD 600
| LD 250 | 6500 | MD 800
| LD 250 | 4800 | MG 600
| LD 250 | 5200 | MG 800
| LD 250 | 7200 | SMD 600 s
| LD 250 | 9600 | SMD 800 s
| LD 250 | 4800 | MG 600 s
| LD 250 | 4800 | MG 800 s
| LD 250 | 8000 | ND 1000
| LD 250 | 8000 | ND 1200
| LD 250 | 6400 | NG 800
| LD 250 | 8000 | NG 1000
| LD 250 | 9600 | NG 1200
| LD 250 | 9400 | SND 800 s
| LD 250 | 10000 | SND 1000 s
| LD 250 | 10000 | SND 1200 s
| LD 250 | 7040 | NG 800 s
| LD 250 | 8800 | NG 1000 s
| LD 250 | 9600 | NG 1200 s
| LD 250 | 8000 | PD 1200
| LD 250 | 8000 | PD 1600
| LD 250 | 9600 | PG 1200
| LD 250 | 9600 | PG 1600
| LD 250 | 10000 | SPD 1400 s
| LD 250 | 10000 | SPD 1600 s
| LD 250 | 9600 | PG 1200 s
| LD 250 | 7680 | PG 1600 s
| LD 250 | 52000 | WL 800 FS1 UL489
| LD 250 | 52000 | WL 1200 FS1 UL489
| LD 250 | 52000 | WL 800 FS2 UL489
| LD 250 | 52000 | WL 1200 FS2 UL489
| LD 250 | 52000 | WL 1600 FS2 UL489
| LD 250 | 52000 | WL 2000 FS2 UL489
| LD 250 | 52000 | WL 2500 FS2 UL489
| LD 250 | 52000 | WL 3000 FS2 UL489
| LD 250 | 68000 | WL 4000 FS3 UL489
| LD 250 | 68000 | WL 5000 FS3 UL489
| LD 250 | 50000 | WL 800 N FS2 UL1066
| LD 250 | 65000 | WL 800 S,H FS2 UL1066
| LD 250 | 85000 | WL 800 L FS2 UL1066
| LD 250 | 20000 | WL 800 F FS2 UL1066
| LD 250 | 50000 | WL 1600 N FS2 UL1066
| LD 250 | 65000 | WL 1600 S,H FS2 UL1066
| LD 250 | 85000 | WL 1600 L FS2 UL1066
| LD 250 | 20000 | WL 1600 F FS2 UL1066
| LD 250 | 65000 | WL 2000 S,H FS2 UL1066
| LD 250 | 85000 | WL 2000 L FS2 UL1066
| LD 250 | 20000 | WL 2000 F FS2 UL1066
| LD 250 | 65000 | WL 3200 S,H FS2 UL1066
| LD 250 | 85000 | WL 3200 L FS2 UL1066
| LD 250 | 100000 | WL 3200 M FS3 UL1066
| LD 250 | 40000 | WL 3200 F FS3 UL1066
| LD 250 | 85000 | WL 4000 H FS3 UL1066
| LD 250 | 100000 | WL 4000 L,M FS3 UL1066
| LD 250 | 40000 | WL 4000 F FS3 UL1066
| LD 250 | 85000 | WL 5000 H FS3 UL1066
| LD 250 | 100000 | WL 5000 L,M FS3 UL1066
| LD 250 | 40000 | WL 5000 F FS3 UL1066
| LD 400 | 6500 | MD 800
| LD 400 | 5200 | MG 800
| LD 400 | 9600 | SMD 800 s
| LD 400 | 8000 | ND 1000
| LD 400 | 8000 | ND 1200
| LD 400 | 6400 | NG 800
| LD 400 | 8000 | NG 1000
| LD 400 | 9600 | NG 1200
| LD 400 | 9400 | SND 800 s
| LD 400 | 10000 | SND 1000 s
| LD 400 | 10000 | SND 1200 s
| LD 400 | 7040 | NG 800 s
| LD 400 | 8800 | NG 1000 s
| LD 400 | 9600 | NG 1200 s
| LD 400 | 8000 | PD 1200
| LD 400 | 8000 | PD 1600
| LD 400 | 9600 | PG 1200
| LD 400 | 9600 | PG 1600
| LD 400 | 10000 | SPD 1400 s
| LD 400 | 10000 | SPD 1600 s
| LD 400 | 9600 | PG 1200 s
| LD 400 | 7680 | PG 1600 s
| LD 400 | 52000 | WL 800 FS1 UL489
| LD 400 | 52000 | WL 1200 FS1 UL489
| LD 400 | 52000 | WL 800 FS2 UL489
| LD 400 | 52000 | WL 1200 FS2 UL489
| LD 400 | 52000 | WL 1600 FS2 UL489
| LD 400 | 52000 | WL 2000 FS2 UL489
| LD 400 | 52000 | WL 2500 FS2 UL489
| LD 400 | 52000 | WL 3000 FS2 UL489
| LD 400 | 68000 | WL 4000 FS3 UL489
| LD 400 | 68000 | WL 5000 FS3 UL489
| LD 400 | 50000 | WL 800 N FS2 UL1066
| LD 400 | 65000 | WL 800 S,H FS2 UL1066
| LD 400 | 85000 | WL 800 L FS2 UL1066
| LD 400 | 20000 | WL 800 F FS2 UL1066
| LD 400 | 50000 | WL 1600 N FS2 UL1066
| LD 400 | 65000 | WL 1600 S,H FS2 UL1066
| LD 400 | 85000 | WL 1600 L FS2 UL1066
| LD 400 | 20000 | WL 1600 F FS2 UL1066
| LD 400 | 65000 | WL 2000 S,H FS2 UL1066
| LD 400 | 85000 | WL 2000 L FS2 UL1066
| LD 400 | 20000 | WL 2000 F FS2 UL1066
| LD 400 | 65000 | WL 3200 S,H FS2 UL1066
| LD 400 | 85000 | WL 3200 L FS2 UL1066
| LD 400 | 100000 | WL 3200 M FS3 UL1066
| LD 400 | 40000 | WL 3200 F FS3 UL1066
| LD 400 | 85000 | WL 4000 H FS3 UL1066
| LD 400 | 100000 | WL 4000 L,M FS3 UL1066
| LD 400 | 40000 | WL 4000 F FS3 UL1066
| LD 400 | 85000 | WL 5000 H FS3 UL1066
| LD 400 | 100000 | WL 5000 L,M FS3 UL1066
| LD 400 | 40000 | WL 5000 F FS3 UL1066
| LD 500 | 8000 | ND 1000
| LD 500 | 8000 | ND 1200
| LD 500 | 8000 | NG 1000
| LD 500 | 9600 | NG 1200
| LD 500 | 10000 | SND 1200 s
| LD 500 | 8800 | NG 1000 s
| LD 500 | 9600 | NG 1200 s
| LD 500 | 8000 | PD 1200
| LD 500 | 8000 | PD 1600
| LD 500 | 9600 | PG 1200
| LD 500 | 9600 | PG 1600
| LD 500 | 10000 | SPD 1400 s
| LD 500 | 10000 | SPD 1600 s
| LD 500 | 9600 | PG 1200 s
| LD 500 | 7680 | PG 1600 s
| LD 500 | 52000 | WL 1200 FS1 UL489
| LD 500 | 52000 | WL 1200 FS2 UL489
| LD 500 | 52000 | WL 1600 FS2 UL489
| LD 500 | 52000 | WL 2000 FS2 UL489
| LD 500 | 52000 | WL 2500 FS2 UL489
| LD 500 | 52000 | WL 3000 FS2 UL489
| LD 500 | 68000 | WL 4000 FS3 UL489
| LD 500 | 68000 | WL 5000 FS3 UL489
| LD 500 | 50000 | WL 1600 N FS2 UL1066
| LD 500 | 65000 | WL 1600 S,H FS2 UL1066
| LD 500 | 85000 | WL 1600 L FS2 UL1066
| LD 500 | 20000 | WL 1600 F FS2 UL1066
| LD 500 | 65000 | WL 2000 S,H FS2 UL1066
| LD 500 | 85000 | WL 2000 L FS2 UL1066
| LD 500 | 20000 | WL 2000 F FS2 UL1066
| LD 500 | 65000 | WL 3200 S,H FS2 UL1066
| LD 500 | 85000 | WL 3200 L FS2 UL1066
| LD 500 | 100000 | WL 3200 M FS3 UL1066
| LD 500 | 40000 | WL 3200 F FS3 UL1066
| LD 500 | 85000 | WL 4000 H FS3 UL1066
| LD 500 | 100000 | WL 4000 L,M FS3 UL1066
| LD 500 | 40000 | WL 4000 F FS3 UL1066
| LD 500 | 85000 | WL 5000 H FS3 UL1066
| LD 500 | 100000 | WL 5000 L,M FS3 UL1066
| LD 500 | 40000 | WL 5000 F FS3 UL1066
| LD 600 | 9600 | NG 1200
| LD 600 | 10000 | SND 1200 s
| LD 600 | 9600 | NG 1200 s
| LD 600 | 8000 | PD 1200
| LD 600 | 8000 | PD 1600
| LD 600 | 9600 | PG 1200
| LD 600 | 9600 | PG 1600
| LD 600 | 10000 | SPD 1400 s
| LD 600 | 10000 | SPD 1600 s
| LD 600 | 9600 | PG 1200 s
| LD 600 | 7680 | PG 1600 s
| LD 600 | 52000 | WL 1200 FS1 UL489
| LD 600 | 52000 | WL 1200 FS2 UL489
| LD 600 | 52000 | WL 1600 FS2 UL489
| LD 600 | 52000 | WL 2000 FS2 UL489
| LD 600 | 52000 | WL 2500 FS2 UL489
| LD 600 | 52000 | WL 3000 FS2 UL489
| LD 600 | 68000 | WL 4000 FS3 UL489
| LD 600 | 68000 | WL 5000 FS3 UL489
| LD 600 | 50000 | WL 1600 N FS2 UL1066
| LD 600 | 65000 | WL 1600 S,H FS2 UL1066
| LD 600 | 85000 | WL 1600 L FS2 UL1066
| LD 600 | 20000 | WL 1600 F FS2 UL1066
| LD 600 | 65000 | WL 2000 S,H FS2 UL1066
| LD 600 | 85000 | WL 2000 L FS2 UL1066
| LD 600 | 20000 | WL 2000 F FS2 UL1066
| LD 600 | 65000 | WL 3200 S,H FS2 UL1066
| LD 600 | 85000 | WL 3200 L FS2 UL1066
| LD 600 | 100000 | WL 3200 M FS3 UL1066
| LD 600 | 40000 | WL 3200 F FS3 UL1066
| LD 600 | 85000 | WL 4000 H FS3 UL1066
| LD 600 | 100000 | WL 4000 L,M FS3 UL1066
| LD 600 | 40000 | WL 4000 F FS3 UL1066
| LD 600 | 85000 | WL 5000 H FS3 UL1066
| LD 600 | 100000 | WL 5000 L,M FS3 UL1066
| LD 600 | 40000 | WL 5000 F FS3 UL1066
| SLD 300 s | 4800 | LD 600
| SLD 300 s | 5200 | SLD 500 s
| SLD 300 s | 6200 | SLD 600 s
| SLD 300 s | 6500 | MD 600
| SLD 300 s | 6500 | MD 800
| SLD 300 s | 4800 | MG 600
| SLD 300 s | 5200 | MG 800
| SLD 300 s | 7200 | SMD 600 s
| SLD 300 s | 9600 | SMD 800 s
| SLD 300 s | 4800 | MG 800 s
| SLD 300 s | 8000 | ND 1000
| SLD 300 s | 8000 | ND 1200
| SLD 300 s | 6400 | NG 800
| SLD 300 s | 8000 | NG 1000
| SLD 300 s | 9600 | NG 1200
| SLD 300 s | 9400 | SND 800 s
| SLD 300 s | 10000 | SND 1000 s
| SLD 300 s | 10000 | SND 1200 s
| SLD 300 s | 7040 | NG 800 s
| SLD 300 s | 8800 | NG 1000 s
| SLD 300 s | 9600 | NG 1200 s
| SLD 300 s | 8000 | PD 1200
| SLD 300 s | 8000 | PD 1600
| SLD 300 s | 9600 | PG 1200
| SLD 300 s | 9600 | PG 1600
| SLD 300 s | 10000 | SPD 1400 s
| SLD 300 s | 10000 | SPD 1600 s
| SLD 300 s | 9600 | PG 1200 s
| SLD 300 s | 7680 | PG 1600 s
| SLD 300 s | 52000 | WL 800 FS1 UL489
| SLD 300 s | 52000 | WL 1200 FS1 UL489
| SLD 300 s | 52000 | WL 800 FS2 UL489
| SLD 300 s | 52000 | WL 1200 FS2 UL489
| SLD 300 s | 52000 | WL 1600 FS2 UL489
| SLD 300 s | 52000 | WL 2000 FS2 UL489
| SLD 300 s | 52000 | WL 2500 FS2 UL489
| SLD 300 s | 52000 | WL 3000 FS2 UL489
| SLD 300 s | 68000 | WL 4000 FS3 UL489
| SLD 300 s | 68000 | WL 5000 FS3 UL489
| SLD 300 s | 50000 | WL 800 N FS2 UL1066
| SLD 300 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 800 L FS2 UL1066
| SLD 300 s | 20000 | WL 800 F FS2 UL1066
| SLD 300 s | 50000 | WL 1600 N FS2 UL1066
| SLD 300 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 1600 L FS2 UL1066
| SLD 300 s | 20000 | WL 1600 F FS2 UL1066
| SLD 300 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 2000 L FS2 UL1066
| SLD 300 s | 20000 | WL 2000 F FS2 UL1066
| SLD 300 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 3200 L FS2 UL1066
| SLD 300 s | 100000 | WL 3200 M FS3 UL1066
| SLD 300 s | 40000 | WL 3200 F FS3 UL1066
| SLD 300 s | 85000 | WL 4000 H FS3 UL1066
| SLD 300 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 300 s | 40000 | WL 4000 F FS3 UL1066
| SLD 300 s | 85000 | WL 5000 H FS3 UL1066
| SLD 300 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 300 s | 40000 | WL 5000 F FS3 UL1066
| SLD 400 s | 6200 | SLD 600 s
| SLD 400 s | 6500 | MD 800
| SLD 400 s | 5200 | MG 800
| SLD 400 s | 7200 | SMD 600 s
| SLD 400 s | 9600 | SMD 800 s
| SLD 400 s | 4800 | MG 800 s
| SLD 400 s | 8000 | ND 1000
| SLD 400 s | 8000 | ND 1200
| SLD 400 s | 6400 | NG 800
| SLD 400 s | 8000 | NG 1000
| SLD 400 s | 9600 | NG 1200
| SLD 400 s | 9400 | SND 800 s
| SLD 400 s | 10000 | SND 1000 s
| SLD 400 s | 10000 | SND 1200 s
| SLD 400 s | 7040 | NG 800 s
| SLD 400 s | 8800 | NG 1000 s
| SLD 400 s | 9600 | NG 1200 s
| SLD 400 s | 8000 | PD 1200
| SLD 400 s | 8000 | PD 1600
| SLD 400 s | 9600 | PG 1200
| SLD 400 s | 9600 | PG 1600
| SLD 400 s | 10000 | SPD 1400 s
| SLD 400 s | 10000 | SPD 1600 s
| SLD 400 s | 9600 | PG 1200 s
| SLD 400 s | 7680 | PG 1600 s
| SLD 400 s | 52000 | WL 800 FS1 UL489
| SLD 400 s | 52000 | WL 1200 FS1 UL489
| SLD 400 s | 52000 | WL 800 FS2 UL489
| SLD 400 s | 52000 | WL 1200 FS2 UL489
| SLD 400 s | 52000 | WL 1600 FS2 UL489
| SLD 400 s | 52000 | WL 2000 FS2 UL489
| SLD 400 s | 52000 | WL 2500 FS2 UL489
| SLD 400 s | 52000 | WL 3000 FS2 UL489
| SLD 400 s | 68000 | WL 4000 FS3 UL489
| SLD 400 s | 68000 | WL 5000 FS3 UL489
| SLD 400 s | 50000 | WL 800 N FS2 UL1066
| SLD 400 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 800 L FS2 UL1066
| SLD 400 s | 20000 | WL 800 F FS2 UL1066
| SLD 400 s | 50000 | WL 1600 N FS2 UL1066
| SLD 400 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 1600 L FS2 UL1066
| SLD 400 s | 20000 | WL 1600 F FS2 UL1066
| SLD 400 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 2000 L FS2 UL1066
| SLD 400 s | 20000 | WL 2000 F FS2 UL1066
| SLD 400 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 3200 L FS2 UL1066
| SLD 400 s | 100000 | WL 3200 M FS3 UL1066
| SLD 400 s | 40000 | WL 3200 F FS3 UL1066
| SLD 400 s | 85000 | WL 4000 H FS3 UL1066
| SLD 400 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 400 s | 40000 | WL 4000 F FS3 UL1066
| SLD 400 s | 85000 | WL 5000 H FS3 UL1066
| SLD 400 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 400 s | 40000 | WL 5000 F FS3 UL1066
| SLD 500 s | 5200 | MG 800
| SLD 500 s | 9600 | SMD 800 s
| SLD 500 s | 8000 | ND 1000
| SLD 500 s | 8000 | ND 1200
| SLD 500 s | 6400 | NG 800
| SLD 500 s | 8000 | NG 1000
| SLD 500 s | 9600 | NG 1200
| SLD 500 s | 9400 | SND 800 s
| SLD 500 s | 10000 | SND 1000 s
| SLD 500 s | 10000 | SND 1200 s
| SLD 500 s | 7040 | NG 800 s
| SLD 500 s | 8800 | NG 1000 s
| SLD 500 s | 9600 | NG 1200 s
| SLD 500 s | 8000 | PD 1200
| SLD 500 s | 8000 | PD 1600
| SLD 500 s | 9600 | PG 1200
| SLD 500 s | 9600 | PG 1600
| SLD 500 s | 10000 | SPD 1400 s
| SLD 500 s | 10000 | SPD 1600 s
| SLD 500 s | 9600 | PG 1200 s
| SLD 500 s | 7680 | PG 1600 s
| SLD 500 s | 52000 | WL 800 FS1 UL489
| SLD 500 s | 52000 | WL 1200 FS1 UL489
| SLD 500 s | 52000 | WL 800 FS2 UL489
| SLD 500 s | 52000 | WL 1200 FS2 UL489
| SLD 500 s | 52000 | WL 1600 FS2 UL489
| SLD 500 s | 52000 | WL 2000 FS2 UL489
| SLD 500 s | 52000 | WL 2500 FS2 UL489
| SLD 500 s | 52000 | WL 3000 FS2 UL489
| SLD 500 s | 68000 | WL 4000 FS3 UL489
| SLD 500 s | 68000 | WL 5000 FS3 UL489
| SLD 500 s | 50000 | WL 800 N FS2 UL1066
| SLD 500 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 800 L FS2 UL1066
| SLD 500 s | 20000 | WL 800 F FS2 UL1066
| SLD 500 s | 50000 | WL 1600 N FS2 UL1066
| SLD 500 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 1600 L FS2 UL1066
| SLD 500 s | 20000 | WL 1600 F FS2 UL1066
| SLD 500 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 2000 L FS2 UL1066
| SLD 500 s | 20000 | WL 2000 F FS2 UL1066
| SLD 500 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 3200 L FS2 UL1066
| SLD 500 s | 100000 | WL 3200 M FS3 UL1066
| SLD 500 s | 40000 | WL 3200 F FS3 UL1066
| SLD 500 s | 85000 | WL 4000 H FS3 UL1066
| SLD 500 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 500 s | 40000 | WL 4000 F FS3 UL1066
| SLD 500 s | 85000 | WL 5000 H FS3 UL1066
| SLD 500 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 500 s | 40000 | WL 5000 F FS3 UL1066
| SLD 600 s | 9600 | SMD 800 s
| SLD 600 s | 8000 | ND 1200
| SLD 600 s | 8000 | NG 1000
| SLD 600 s | 9600 | NG 1200
| SLD 600 s | 9400 | SND 800 s
| SLD 600 s | 10000 | SND 1000 s
| SLD 600 s | 10000 | SND 1200 s
| SLD 600 s | 7040 | NG 800 s
| SLD 600 s | 8800 | NG 1000 s
| SLD 600 s | 9600 | NG 1200 s
| SLD 600 s | 8000 | PD 1200
| SLD 600 s | 8000 | PD 1600
| SLD 600 s | 9600 | PG 1200
| SLD 600 s | 9600 | PG 1600
| SLD 600 s | 10000 | SPD 1400 s
| SLD 600 s | 10000 | SPD 1600 s
| SLD 600 s | 9600 | PG 1200 s
| SLD 600 s | 7680 | PG 1600 s
| SLD 600 s | 52000 | WL 800 FS1 UL489
| SLD 600 s | 52000 | WL 1200 FS1 UL489
| SLD 600 s | 52000 | WL 800 FS2 UL489
| SLD 600 s | 52000 | WL 1200 FS2 UL489
| SLD 600 s | 52000 | WL 1600 FS2 UL489
| SLD 600 s | 52000 | WL 2000 FS2 UL489
| SLD 600 s | 52000 | WL 2500 FS2 UL489
| SLD 600 s | 52000 | WL 3000 FS2 UL489
| SLD 600 s | 68000 | WL 4000 FS3 UL489
| SLD 600 s | 68000 | WL 5000 FS3 UL489
| SLD 600 s | 50000 | WL 800 N FS2 UL1066
| SLD 600 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 800 L FS2 UL1066
| SLD 600 s | 20000 | WL 800 F FS2 UL1066
| SLD 600 s | 50000 | WL 1600 N FS2 UL1066
| SLD 600 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 1600 L FS2 UL1066
| SLD 600 s | 20000 | WL 1600 F FS2 UL1066
| SLD 600 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 2000 L FS2 UL1066
| SLD 600 s | 20000 | WL 2000 F FS2 UL1066
| SLD 600 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 3200 L FS2 UL1066
| SLD 600 s | 100000 | WL 3200 M FS3 UL1066
| SLD 600 s | 40000 | WL 3200 F FS3 UL1066
| SLD 600 s | 85000 | WL 4000 H FS3 UL1066
| SLD 600 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 600 s | 40000 | WL 4000 F FS3 UL1066
| SLD 600 s | 85000 | WL 5000 H FS3 UL1066
| SLD 600 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 600 s | 40000 | WL 5000 F FS3 UL1066
| MD 500 | 9600 | NG 1200 s
| MD 500 | 10000 | SPD 1400 s
| MD 500 | 10000 | SPD 1600 s
| MD 500 | 9600 | PG 1200 s
| MD 500 | 7680 | PG 1600 s
| MD 500 | 52000 | WL 1600 FS2 UL489
| MD 500 | 52000 | WL 2000 FS2 UL489
| MD 500 | 52000 | WL 2500 FS2 UL489
| MD 500 | 52000 | WL 3000 FS2 UL489
| MD 500 | 68000 | WL 4000 FS3 UL489
| MD 500 | 68000 | WL 5000 FS3 UL489
| MD 500 | 50000 | WL 1600 N FS2 UL1066
| MD 500 | 65000 | WL 1600 S,H FS2 UL1066
| MD 500 | 85000 | WL 1600 L FS2 UL1066
| MD 500 | 20000 | WL 1600 F FS2 UL1066
| MD 500 | 65000 | WL 2000 S,H FS2 UL1066
| MD 500 | 85000 | WL 2000 L FS2 UL1066
| MD 500 | 20000 | WL 2000 F FS2 UL1066
| MD 500 | 65000 | WL 3200 S,H FS2 UL1066
| MD 500 | 85000 | WL 3200 L FS2 UL1066
| MD 500 | 100000 | WL 3200 M FS3 UL1066
| MD 500 | 40000 | WL 3200 F FS3 UL1066
| MD 500 | 85000 | WL 4000 H FS3 UL1066
| MD 500 | 100000 | WL 4000 L,M FS3 UL1066
| MD 500 | 40000 | WL 4000 F FS3 UL1066
| MD 500 | 85000 | WL 5000 H FS3 UL1066
| MD 500 | 100000 | WL 5000 L,M FS3 UL1066
| MD 500 | 40000 | WL 5000 F FS3 UL1066
| MD 600 | 10000 | SPD 1600 s
| MD 600 | 52000 | WL 1600 FS2 UL489
| MD 600 | 52000 | WL 2000 FS2 UL489
| MD 600 | 52000 | WL 2500 FS2 UL489
| MD 600 | 52000 | WL 3000 FS2 UL489
| MD 600 | 68000 | WL 4000 FS3 UL489
| MD 600 | 68000 | WL 5000 FS3 UL489
| MD 600 | 50000 | WL 1600 N FS2 UL1066
| MD 600 | 65000 | WL 1600 S,H FS2 UL1066
| MD 600 | 85000 | WL 1600 L FS2 UL1066
| MD 600 | 20000 | WL 1600 F FS2 UL1066
| MD 600 | 65000 | WL 2000 S,H FS2 UL1066
| MD 600 | 85000 | WL 2000 L FS2 UL1066
| MD 600 | 20000 | WL 2000 F FS2 UL1066
| MD 600 | 65000 | WL 3200 S,H FS2 UL1066
| MD 600 | 85000 | WL 3200 L FS2 UL1066
| MD 600 | 100000 | WL 3200 M FS3 UL1066
| MD 600 | 40000 | WL 3200 F FS3 UL1066
| MD 600 | 85000 | WL 4000 H FS3 UL1066
| MD 600 | 100000 | WL 4000 L,M FS3 UL1066
| MD 600 | 40000 | WL 4000 F FS3 UL1066
| MD 600 | 85000 | WL 5000 H FS3 UL1066
| MD 600 | 100000 | WL 5000 L,M FS3 UL1066
| MD 600 | 40000 | WL 5000 F FS3 UL1066
| MD 800 | 52000 | WL 2000 FS2 UL489
| MD 800 | 52000 | WL 2500 FS2 UL489
| MD 800 | 52000 | WL 3000 FS2 UL489
| MD 800 | 68000 | WL 4000 FS3 UL489
| MD 800 | 68000 | WL 5000 FS3 UL489
| MD 800 | 65000 | WL 2000 S,H FS2 UL1066
| MD 800 | 85000 | WL 2000 L FS2 UL1066
| MD 800 | 20000 | WL 2000 F FS2 UL1066
| MD 800 | 65000 | WL 3200 S,H FS2 UL1066
| MD 800 | 85000 | WL 3200 L FS2 UL1066
| MD 800 | 100000 | WL 3200 M FS3 UL1066
| MD 800 | 40000 | WL 3200 F FS3 UL1066
| MD 800 | 85000 | WL 4000 H FS3 UL1066
| MD 800 | 100000 | WL 4000 L,M FS3 UL1066
| MD 800 | 40000 | WL 4000 F FS3 UL1066
| MD 800 | 85000 | WL 5000 H FS3 UL1066
| MD 800 | 100000 | WL 5000 L,M FS3 UL1066
| MD 800 | 40000 | WL 5000 F FS3 UL1066
| MG 600 | 52000 | WL 2000 FS2 UL489
| MG 600 | 52000 | WL 2500 FS2 UL489
| MG 600 | 52000 | WL 3000 FS2 UL489
| MG 600 | 68000 | WL 4000 FS3 UL489
| MG 600 | 68000 | WL 5000 FS3 UL489
| MG 600 | 65000 | WL 2000 S,H FS2 UL1066
| MG 600 | 85000 | WL 2000 L FS2 UL1066
| MG 600 | 20000 | WL 2000 F FS2 UL1066
| MG 600 | 65000 | WL 3200 S,H FS2 UL1066
| MG 600 | 85000 | WL 3200 L FS2 UL1066
| MG 600 | 100000 | WL 3200 M FS3 UL1066
| MG 600 | 40000 | WL 3200 F FS3 UL1066
| MG 600 | 85000 | WL 4000 H FS3 UL1066
| MG 600 | 100000 | WL 4000 L,M FS3 UL1066
| MG 600 | 40000 | WL 4000 F FS3 UL1066
| MG 600 | 85000 | WL 5000 H FS3 UL1066
| MG 600 | 100000 | WL 5000 L,M FS3 UL1066
| MG 600 | 40000 | WL 5000 F FS3 UL1066
| MG 800 | 52000 | WL 2500 FS2 UL489
| MG 800 | 52000 | WL 3000 FS2 UL489
| MG 800 | 68000 | WL 4000 FS3 UL489
| MG 800 | 68000 | WL 5000 FS3 UL489
| MG 800 | 65000 | WL 3200 S,H FS2 UL1066
| MG 800 | 85000 | WL 3200 L FS2 UL1066
| MG 800 | 100000 | WL 3200 M FS3 UL1066
| MG 800 | 40000 | WL 3200 F FS3 UL1066
| MG 800 | 85000 | WL 4000 H FS3 UL1066
| MG 800 | 100000 | WL 4000 L,M FS3 UL1066
| MG 800 | 40000 | WL 4000 F FS3 UL1066
| MG 800 | 85000 | WL 5000 H FS3 UL1066
| MG 800 | 100000 | WL 5000 L,M FS3 UL1066
| MG 800 | 40000 | WL 5000 F FS3 UL1066
| SMD 600 s | 9600 | SMD 800 s
| SMD 600 s | 8000 | ND 1200
| SMD 600 s | 8000 | NG 1000
| SMD 600 s | 9600 | NG 1200
| SMD 600 s | 9400 | SND 800 s
| SMD 600 s | 10000 | SND 1000 s
| SMD 600 s | 10000 | SND 1200 s
| SMD 600 s | 7040 | NG 800 s
| SMD 600 s | 8800 | NG 1000 s
| SMD 600 s | 9600 | NG 1200 s
| SMD 600 s | 8000 | PD 1200
| SMD 600 s | 8000 | PD 1600
| SMD 600 s | 9600 | PG 1200
| SMD 600 s | 9600 | PG 1600
| SMD 600 s | 10000 | SPD 1400 s
| SMD 600 s | 10000 | SPD 1600 s
| SMD 600 s | 9600 | PG 1200 s
| SMD 600 s | 7680 | PG 1600 s
| SMD 600 s | 52000 | WL 800 FS1 UL489
| SMD 600 s | 52000 | WL 1200 FS1 UL489
| SMD 600 s | 52000 | WL 800 FS2 UL489
| SMD 600 s | 52000 | WL 1200 FS2 UL489
| SMD 600 s | 52000 | WL 1600 FS2 UL489
| SMD 600 s | 52000 | WL 2000 FS2 UL489
| SMD 600 s | 52000 | WL 2500 FS2 UL489
| SMD 600 s | 52000 | WL 3000 FS2 UL489
| SMD 600 s | 68000 | WL 4000 FS3 UL489
| SMD 600 s | 68000 | WL 5000 FS3 UL489
| SMD 600 s | 50000 | WL 800 N FS2 UL1066
| SMD 600 s | 65000 | WL 800 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 800 L FS2 UL1066
| SMD 600 s | 20000 | WL 800 F FS2 UL1066
| SMD 600 s | 50000 | WL 1600 N FS2 UL1066
| SMD 600 s | 65000 | WL 1600 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 1600 L FS2 UL1066
| SMD 600 s | 20000 | WL 1600 F FS2 UL1066
| SMD 600 s | 65000 | WL 2000 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 2000 L FS2 UL1066
| SMD 600 s | 20000 | WL 2000 F FS2 UL1066
| SMD 600 s | 65000 | WL 3200 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 3200 L FS2 UL1066
| SMD 600 s | 100000 | WL 3200 M FS3 UL1066
| SMD 600 s | 40000 | WL 3200 F FS3 UL1066
| SMD 600 s | 85000 | WL 4000 H FS3 UL1066
| SMD 600 s | 100000 | WL 4000 L,M FS3 UL1066
| SMD 600 s | 40000 | WL 4000 F FS3 UL1066
| SMD 600 s | 85000 | WL 5000 H FS3 UL1066
| SMD 600 s | 100000 | WL 5000 L,M FS3 UL1066
| SMD 600 s | 40000 | WL 5000 F FS3 UL1066
| SMD 800 s | 10000 | SND 1200 s
| SMD 800 s | 9600 | NG 1200 s
| SMD 800 s | 9600 | PG 1200
| SMD 800 s | 9600 | PG 1600
| SMD 800 s | 10000 | SPD 1400 s
| SMD 800 s | 10000 | SPD 1600 s
| SMD 800 s | 9600 | PG 1200 s
| SMD 800 s | 7680 | PG 1600 s
| SMD 800 s | 52000 | WL 1200 FS1 UL489
| SMD 800 s | 52000 | WL 1200 FS2 UL489
| SMD 800 s | 52000 | WL 1600 FS2 UL489
| SMD 800 s | 52000 | WL 2000 FS2 UL489
| SMD 800 s | 52000 | WL 2500 FS2 UL489
| SMD 800 s | 52000 | WL 3000 FS2 UL489
| SMD 800 s | 68000 | WL 4000 FS3 UL489
| SMD 800 s | 68000 | WL 5000 FS3 UL489
| SMD 800 s | 50000 | WL 1600 N FS2 UL1066
| SMD 800 s | 65000 | WL 1600 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 1600 L FS2 UL1066
| SMD 800 s | 20000 | WL 1600 F FS2 UL1066
| SMD 800 s | 65000 | WL 2000 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 2000 L FS2 UL1066
| SMD 800 s | 20000 | WL 2000 F FS2 UL1066
| SMD 800 s | 65000 | WL 3200 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 3200 L FS2 UL1066
| SMD 800 s | 100000 | WL 3200 M FS3 UL1066
| SMD 800 s | 40000 | WL 3200 F FS3 UL1066
| SMD 800 s | 85000 | WL 4000 H FS3 UL1066
| SMD 800 s | 100000 | WL 4000 L,M FS3 UL1066
| SMD 800 s | 40000 | WL 4000 F FS3 UL1066
| SMD 800 s | 85000 | WL 5000 H FS3 UL1066
| SMD 800 s | 100000 | WL 5000 L,M FS3 UL1066
| SMD 800 s | 40000 | WL 5000 F FS3 UL1066
| MG 600 s | 8000 | ND 1200
| MG 600 s | 9600 | NG 1200
| MG 600 s | 10000 | SND 1000 s
| MG 600 s | 10000 | SND 1200 s
| MG 600 s | 8800 | NG 1000 s
| MG 600 s | 9600 | NG 1200 s
| MG 600 s | 8000 | PD 1200
| MG 600 s | 8000 | PD 1600
| MG 600 s | 9600 | PG 1200
| MG 600 s | 9600 | PG 1600
| MG 600 s | 10000 | SPD 1400 s
| MG 600 s | 10000 | SPD 1600 s
| MG 600 s | 9600 | PG 1200 s
| MG 600 s | 7680 | PG 1600 s
| MG 600 s | 52000 | WL 800 FS1 UL489
| MG 600 s | 52000 | WL 1200 FS1 UL489
| MG 600 s | 52000 | WL 800 FS2 UL489
| MG 600 s | 52000 | WL 1200 FS2 UL489
| MG 600 s | 52000 | WL 1600 FS2 UL489
| MG 600 s | 52000 | WL 2000 FS2 UL489
| MG 600 s | 52000 | WL 2500 FS2 UL489
| MG 600 s | 52000 | WL 3000 FS2 UL489
| MG 600 s | 68000 | WL 4000 FS3 UL489
| MG 600 s | 68000 | WL 5000 FS3 UL489
| MG 600 s | 50000 | WL 800 N FS2 UL1066
| MG 600 s | 65000 | WL 800 S,H FS2 UL1066
| MG 600 s | 85000 | WL 800 L FS2 UL1066
| MG 600 s | 20000 | WL 800 F FS2 UL1066
| MG 600 s | 50000 | WL 1600 N FS2 UL1066
| MG 600 s | 65000 | WL 1600 S,H FS2 UL1066
| MG 600 s | 85000 | WL 1600 L FS2 UL1066
| MG 600 s | 20000 | WL 1600 F FS2 UL1066
| MG 600 s | 65000 | WL 2000 S,H FS2 UL1066
| MG 600 s | 85000 | WL 2000 L FS2 UL1066
| MG 600 s | 20000 | WL 2000 F FS2 UL1066
| MG 600 s | 65000 | WL 3200 S,H FS2 UL1066
| MG 600 s | 85000 | WL 3200 L FS2 UL1066
| MG 600 s | 100000 | WL 3200 M FS3 UL1066
| MG 600 s | 40000 | WL 3200 F FS3 UL1066
| MG 600 s | 85000 | WL 4000 H FS3 UL1066
| MG 600 s | 100000 | WL 4000 L,M FS3 UL1066
| MG 600 s | 40000 | WL 4000 F FS3 UL1066
| MG 600 s | 85000 | WL 5000 H FS3 UL1066
| MG 600 s | 100000 | WL 5000 L,M FS3 UL1066
| MG 600 s | 40000 | WL 5000 F FS3 UL1066
| MG 800 s | 10000 | SND 1200 s
| MG 800 s | 8800 | NG 1000 s
| MG 800 s | 9600 | NG 1200 s
| MG 800 s | 8000 | PD 1600
| MG 800 s | 9600 | PG 1600
| MG 800 s | 10000 | SPD 1400 s
| MG 800 s | 10000 | SPD 1600 s
| MG 800 s | 9600 | PG 1200 s
| MG 800 s | 7680 | PG 1600 s
| MG 800 s | 52000 | WL 1200 FS1 UL489
| MG 800 s | 52000 | WL 1200 FS2 UL489
| MG 800 s | 52000 | WL 1600 FS2 UL489
| MG 800 s | 52000 | WL 2000 FS2 UL489
| MG 800 s | 52000 | WL 2500 FS2 UL489
| MG 800 s | 52000 | WL 3000 FS2 UL489
| MG 800 s | 68000 | WL 4000 FS3 UL489
| MG 800 s | 68000 | WL 5000 FS3 UL489
| MG 800 s | 50000 | WL 1600 N FS2 UL1066
| MG 800 s | 65000 | WL 1600 S,H FS2 UL1066
| MG 800 s | 85000 | WL 1600 L FS2 UL1066
| MG 800 s | 20000 | WL 1600 F FS2 UL1066
| MG 800 s | 65000 | WL 2000 S,H FS2 UL1066
| MG 800 s | 85000 | WL 2000 L FS2 UL1066
| MG 800 s | 20000 | WL 2000 F FS2 UL1066
| MG 800 s | 65000 | WL 3200 S,H FS2 UL1066
| MG 800 s | 85000 | WL 3200 L FS2 UL1066
| MG 800 s | 100000 | WL 3200 M FS3 UL1066
| MG 800 s | 40000 | WL 3200 F FS3 UL1066
| MG 800 s | 85000 | WL 4000 H FS3 UL1066
| MG 800 s | 100000 | WL 4000 L,M FS3 UL1066
| MG 800 s | 40000 | WL 4000 F FS3 UL1066
| MG 800 s | 85000 | WL 5000 H FS3 UL1066
| MG 800 s | 100000 | WL 5000 L,M FS3 UL1066
| MG 800 s | 40000 | WL 5000 F FS3 UL1066
| ND 1000 | 52000 | WL 2500 FS2 UL489
| ND 1000 | 52000 | WL 3000 FS2 UL489
| ND 1000 | 68000 | WL 4000 FS3 UL489
| ND 1000 | 68000 | WL 5000 FS3 UL489
| ND 1000 | 65000 | WL 3200 S,H FS2 UL1066
| ND 1000 | 85000 | WL 3200 L FS2 UL1066
| ND 1000 | 100000 | WL 3200 M FS3 UL1066
| ND 1000 | 40000 | WL 3200 F FS3 UL1066
| ND 1000 | 85000 | WL 4000 H FS3 UL1066
| ND 1000 | 100000 | WL 4000 L,M FS3 UL1066
| ND 1000 | 40000 | WL 4000 F FS3 UL1066
| ND 1000 | 85000 | WL 5000 H FS3 UL1066
| ND 1000 | 100000 | WL 5000 L,M FS3 UL1066
| ND 1000 | 40000 | WL 5000 F FS3 UL1066
| ND 1200 | 52000 | WL 2500 FS2 UL489
| ND 1200 | 52000 | WL 3000 FS2 UL489
| ND 1200 | 68000 | WL 4000 FS3 UL489
| ND 1200 | 68000 | WL 5000 FS3 UL489
| ND 1200 | 65000 | WL 3200 S,H FS2 UL1066
| ND 1200 | 85000 | WL 3200 L FS2 UL1066
| ND 1200 | 100000 | WL 3200 M FS3 UL1066
| ND 1200 | 40000 | WL 3200 F FS3 UL1066
| ND 1200 | 85000 | WL 4000 H FS3 UL1066
| ND 1200 | 100000 | WL 4000 L,M FS3 UL1066
| ND 1200 | 40000 | WL 4000 F FS3 UL1066
| ND 1200 | 85000 | WL 5000 H FS3 UL1066
| ND 1200 | 100000 | WL 5000 L,M FS3 UL1066
| ND 1200 | 40000 | WL 5000 F FS3 UL1066
| NG 800 | 52000 | WL 2000 FS2 UL489
| NG 800 | 52000 | WL 2500 FS2 UL489
| NG 800 | 52000 | WL 3000 FS2 UL489
| NG 800 | 68000 | WL 4000 FS3 UL489
| NG 800 | 68000 | WL 5000 FS3 UL489
| NG 800 | 65000 | WL 2000 S,H FS2 UL1066
| NG 800 | 85000 | WL 2000 L FS2 UL1066
| NG 800 | 20000 | WL 2000 F FS2 UL1066
| NG 800 | 65000 | WL 3200 S,H FS2 UL1066
| NG 800 | 85000 | WL 3200 L FS2 UL1066
| NG 800 | 100000 | WL 3200 M FS3 UL1066
| NG 800 | 40000 | WL 3200 F FS3 UL1066
| NG 800 | 85000 | WL 4000 H FS3 UL1066
| NG 800 | 100000 | WL 4000 L,M FS3 UL1066
| NG 800 | 40000 | WL 4000 F FS3 UL1066
| NG 800 | 85000 | WL 5000 H FS3 UL1066
| NG 800 | 100000 | WL 5000 L,M FS3 UL1066
| NG 800 | 40000 | WL 5000 F FS3 UL1066
| NG 1000 | 52000 | WL 2500 FS2 UL489
| NG 1000 | 52000 | WL 3000 FS2 UL489
| NG 1000 | 68000 | WL 4000 FS3 UL489
| NG 1000 | 68000 | WL 5000 FS3 UL489
| NG 1000 | 65000 | WL 3200 S,H FS2 UL1066
| NG 1000 | 85000 | WL 3200 L FS2 UL1066
| NG 1000 | 100000 | WL 3200 M FS3 UL1066
| NG 1000 | 40000 | WL 3200 F FS3 UL1066
| NG 1000 | 85000 | WL 4000 H FS3 UL1066
| NG 1000 | 100000 | WL 4000 L,M FS3 UL1066
| NG 1000 | 40000 | WL 4000 F FS3 UL1066
| NG 1000 | 85000 | WL 5000 H FS3 UL1066
| NG 1000 | 100000 | WL 5000 L,M FS3 UL1066
| NG 1000 | 40000 | WL 5000 F FS3 UL1066
| NG 1200 | 52000 | WL 3000 FS2 UL489
| NG 1200 | 68000 | WL 4000 FS3 UL489
| NG 1200 | 68000 | WL 5000 FS3 UL489
| NG 1200 | 65000 | WL 3200 S,H FS2 UL1066
| NG 1200 | 85000 | WL 3200 L FS2 UL1066
| NG 1200 | 100000 | WL 3200 M FS3 UL1066
| NG 1200 | 40000 | WL 3200 F FS3 UL1066
| NG 1200 | 85000 | WL 4000 H FS3 UL1066
| NG 1200 | 100000 | WL 4000 L,M FS3 UL1066
| NG 1200 | 40000 | WL 4000 F FS3 UL1066
| NG 1200 | 85000 | WL 5000 H FS3 UL1066
| NG 1200 | 100000 | WL 5000 L,M FS3 UL1066
| NG 1200 | 40000 | WL 5000 F FS3 UL1066
| SND 800 s | 9600 | NG 1200 s
| SND 800 s | 9600 | PG 1600
| SND 800 s | 10000 | SPD 1400 s
| SND 800 s | 10000 | SPD 1600 s
| SND 800 s | 9600 | PG 1200 s
| SND 800 s | 7680 | PG 1600 s
| SND 800 s | 52000 | WL 1200 FS1 UL489
| SND 800 s | 52000 | WL 1200 FS2 UL489
| SND 800 s | 52000 | WL 1600 FS2 UL489
| SND 800 s | 52000 | WL 2000 FS2 UL489
| SND 800 s | 52000 | WL 2500 FS2 UL489
| SND 800 s | 52000 | WL 3000 FS2 UL489
| SND 800 s | 68000 | WL 4000 FS3 UL489
| SND 800 s | 68000 | WL 5000 FS3 UL489
| SND 800 s | 50000 | WL 1600 N FS2 UL1066
| SND 800 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 800 s | 85000 | WL 1600 L FS2 UL1066
| SND 800 s | 20000 | WL 1600 F FS2 UL1066
| SND 800 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 800 s | 85000 | WL 2000 L FS2 UL1066
| SND 800 s | 20000 | WL 2000 F FS2 UL1066
| SND 800 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 800 s | 85000 | WL 3200 L FS2 UL1066
| SND 800 s | 100000 | WL 3200 M FS3 UL1066
| SND 800 s | 40000 | WL 3200 F FS3 UL1066
| SND 800 s | 85000 | WL 4000 H FS3 UL1066
| SND 800 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 800 s | 40000 | WL 4000 F FS3 UL1066
| SND 800 s | 85000 | WL 5000 H FS3 UL1066
| SND 800 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 800 s | 40000 | WL 5000 F FS3 UL1066
| SND 1000 s | 10000 | SPD 1400 s
| SND 1000 s | 10000 | SPD 1600 s
| SND 1000 s | 52000 | WL 1600 FS2 UL489
| SND 1000 s | 52000 | WL 2000 FS2 UL489
| SND 1000 s | 52000 | WL 2500 FS2 UL489
| SND 1000 s | 52000 | WL 3000 FS2 UL489
| SND 1000 s | 68000 | WL 4000 FS3 UL489
| SND 1000 s | 68000 | WL 5000 FS3 UL489
| SND 1000 s | 50000 | WL 1600 N FS2 UL1066
| SND 1000 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 1600 L FS2 UL1066
| SND 1000 s | 20000 | WL 1600 F FS2 UL1066
| SND 1000 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 2000 L FS2 UL1066
| SND 1000 s | 20000 | WL 2000 F FS2 UL1066
| SND 1000 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 3200 L FS2 UL1066
| SND 1000 s | 100000 | WL 3200 M FS3 UL1066
| SND 1000 s | 40000 | WL 3200 F FS3 UL1066
| SND 1000 s | 85000 | WL 4000 H FS3 UL1066
| SND 1000 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 1000 s | 40000 | WL 4000 F FS3 UL1066
| SND 1000 s | 85000 | WL 5000 H FS3 UL1066
| SND 1000 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 1000 s | 40000 | WL 5000 F FS3 UL1066
| SND 1200 s | 52000 | WL 1600 FS2 UL489
| SND 1200 s | 52000 | WL 2000 FS2 UL489
| SND 1200 s | 52000 | WL 2500 FS2 UL489
| SND 1200 s | 52000 | WL 3000 FS2 UL489
| SND 1200 s | 68000 | WL 4000 FS3 UL489
| SND 1200 s | 68000 | WL 5000 FS3 UL489
| SND 1200 s | 50000 | WL 1600 N FS2 UL1066
| SND 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 1600 L FS2 UL1066
| SND 1200 s | 20000 | WL 1600 F FS2 UL1066
| SND 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 2000 L FS2 UL1066
| SND 1200 s | 20000 | WL 2000 F FS2 UL1066
| SND 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 3200 L FS2 UL1066
| SND 1200 s | 100000 | WL 3200 M FS3 UL1066
| SND 1200 s | 40000 | WL 3200 F FS3 UL1066
| SND 1200 s | 85000 | WL 4000 H FS3 UL1066
| SND 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 1200 s | 40000 | WL 4000 F FS3 UL1066
| SND 1200 s | 85000 | WL 5000 H FS3 UL1066
| SND 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 1200 s | 40000 | WL 5000 F FS3 UL1066
| NG 800 s | 10000 | SPD 1400 s
| NG 800 s | 10000 | SPD 1600 s
| NG 800 s | 52000 | WL 1200 FS1 UL489
| NG 800 s | 52000 | WL 1200 FS2 UL489
| NG 800 s | 52000 | WL 1600 FS2 UL489
| NG 800 s | 52000 | WL 2000 FS2 UL489
| NG 800 s | 52000 | WL 2500 FS2 UL489
| NG 800 s | 52000 | WL 3000 FS2 UL489
| NG 800 s | 68000 | WL 4000 FS3 UL489
| NG 800 s | 68000 | WL 5000 FS3 UL489
| NG 800 s | 50000 | WL 1600 N FS2 UL1066
| NG 800 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 800 s | 85000 | WL 1600 L FS2 UL1066
| NG 800 s | 20000 | WL 1600 F FS2 UL1066
| NG 800 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 800 s | 85000 | WL 2000 L FS2 UL1066
| NG 800 s | 20000 | WL 2000 F FS2 UL1066
| NG 800 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 800 s | 85000 | WL 3200 L FS2 UL1066
| NG 800 s | 100000 | WL 3200 M FS3 UL1066
| NG 800 s | 40000 | WL 3200 F FS3 UL1066
| NG 800 s | 85000 | WL 4000 H FS3 UL1066
| NG 800 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 800 s | 40000 | WL 4000 F FS3 UL1066
| NG 800 s | 85000 | WL 5000 H FS3 UL1066
| NG 800 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 800 s | 40000 | WL 5000 F FS3 UL1066
| NG 1000 s | 52000 | WL 1600 FS2 UL489
| NG 1000 s | 52000 | WL 2000 FS2 UL489
| NG 1000 s | 52000 | WL 2500 FS2 UL489
| NG 1000 s | 52000 | WL 3000 FS2 UL489
| NG 1000 s | 68000 | WL 4000 FS3 UL489
| NG 1000 s | 68000 | WL 5000 FS3 UL489
| NG 1000 s | 50000 | WL 1600 N FS2 UL1066
| NG 1000 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 1600 L FS2 UL1066
| NG 1000 s | 20000 | WL 1600 F FS2 UL1066
| NG 1000 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 2000 L FS2 UL1066
| NG 1000 s | 20000 | WL 2000 F FS2 UL1066
| NG 1000 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 3200 L FS2 UL1066
| NG 1000 s | 100000 | WL 3200 M FS3 UL1066
| NG 1000 s | 40000 | WL 3200 F FS3 UL1066
| NG 1000 s | 85000 | WL 4000 H FS3 UL1066
| NG 1000 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 1000 s | 40000 | WL 4000 F FS3 UL1066
| NG 1000 s | 85000 | WL 5000 H FS3 UL1066
| NG 1000 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 1000 s | 40000 | WL 5000 F FS3 UL1066
| NG 1200 s | 52000 | WL 1600 FS2 UL489
| NG 1200 s | 52000 | WL 2000 FS2 UL489
| NG 1200 s | 52000 | WL 2500 FS2 UL489
| NG 1200 s | 52000 | WL 3000 FS2 UL489
| NG 1200 s | 68000 | WL 4000 FS3 UL489
| NG 1200 s | 68000 | WL 5000 FS3 UL489
| NG 1200 s | 50000 | WL 1600 N FS2 UL1066
| NG 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 1600 L FS2 UL1066
| NG 1200 s | 20000 | WL 1600 F FS2 UL1066
| NG 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 2000 L FS2 UL1066
| NG 1200 s | 20000 | WL 2000 F FS2 UL1066
| NG 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 3200 L FS2 UL1066
| NG 1200 s | 100000 | WL 3200 M FS3 UL1066
| NG 1200 s | 40000 | WL 3200 F FS3 UL1066
| NG 1200 s | 85000 | WL 4000 H FS3 UL1066
| NG 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 1200 s | 40000 | WL 4000 F FS3 UL1066
| NG 1200 s | 85000 | WL 5000 H FS3 UL1066
| NG 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 1200 s | 40000 | WL 5000 F FS3 UL1066
| PD 1200 | 52000 | WL 2500 FS2 UL489
| PD 1200 | 52000 | WL 3000 FS2 UL489
| PD 1200 | 68000 | WL 4000 FS3 UL489
| PD 1200 | 68000 | WL 5000 FS3 UL489
| PD 1200 | 65000 | WL 3200 S,H FS2 UL1066
| PD 1200 | 85000 | WL 3200 L FS2 UL1066
| PD 1200 | 100000 | WL 3200 M FS3 UL1066
| PD 1200 | 40000 | WL 3200 F FS3 UL1066
| PD 1200 | 85000 | WL 4000 H FS3 UL1066
| PD 1200 | 100000 | WL 4000 L,M FS3 UL1066
| PD 1200 | 40000 | WL 4000 F FS3 UL1066
| PD 1200 | 85000 | WL 5000 H FS3 UL1066
| PD 1200 | 100000 | WL 5000 L,M FS3 UL1066
| PD 1200 | 40000 | WL 5000 F FS3 UL1066
| PD 1600 | 68000 | WL 4000 FS3 UL489
| PD 1600 | 68000 | WL 5000 FS3 UL489
| PD 1600 | 65000 | WL 3200 S,H FS2 UL1066
| PD 1600 | 85000 | WL 3200 L FS2 UL1066
| PD 1600 | 100000 | WL 3200 M FS3 UL1066
| PD 1600 | 40000 | WL 3200 F FS3 UL1066
| PD 1600 | 85000 | WL 4000 H FS3 UL1066
| PD 1600 | 100000 | WL 4000 L,M FS3 UL1066
| PD 1600 | 40000 | WL 4000 F FS3 UL1066
| PD 1600 | 85000 | WL 5000 H FS3 UL1066
| PD 1600 | 100000 | WL 5000 L,M FS3 UL1066
| PD 1600 | 40000 | WL 5000 F FS3 UL1066
| PG 1200 | 52000 | WL 3000 FS2 UL489
| PG 1200 | 68000 | WL 4000 FS3 UL489
| PG 1200 | 68000 | WL 5000 FS3 UL489
| PG 1200 | 65000 | WL 3200 S,H FS2 UL1066
| PG 1200 | 85000 | WL 3200 L FS2 UL1066
| PG 1200 | 100000 | WL 3200 M FS3 UL1066
| PG 1200 | 40000 | WL 3200 F FS3 UL1066
| PG 1200 | 85000 | WL 4000 H FS3 UL1066
| PG 1200 | 100000 | WL 4000 L,M FS3 UL1066
| PG 1200 | 40000 | WL 4000 F FS3 UL1066
| PG 1200 | 85000 | WL 5000 H FS3 UL1066
| PG 1200 | 100000 | WL 5000 L,M FS3 UL1066
| PG 1200 | 40000 | WL 5000 F FS3 UL1066
| PG 1600 | 68000 | WL 4000 FS3 UL489
| PG 1600 | 68000 | WL 5000 FS3 UL489
| PG 1600 | 85000 | WL 4000 H FS3 UL1066
| PG 1600 | 100000 | WL 4000 L,M FS3 UL1066
| PG 1600 | 40000 | WL 4000 F FS3 UL1066
| PG 1600 | 85000 | WL 5000 H FS3 UL1066
| PG 1600 | 100000 | WL 5000 L,M FS3 UL1066
| PG 1600 | 40000 | WL 5000 F FS3 UL1066
| SPD 1400 s | 52000 | WL 2000 FS2 UL489
| SPD 1400 s | 52000 | WL 2500 FS2 UL489
| SPD 1400 s | 52000 | WL 3000 FS2 UL489
| SPD 1400 s | 68000 | WL 4000 FS3 UL489
| SPD 1400 s | 68000 | WL 5000 FS3 UL489
| SPD 1400 s | 65000 | WL 2000 S,H FS2 UL1066
| SPD 1400 s | 85000 | WL 2000 L FS2 UL1066
| SPD 1400 s | 20000 | WL 2000 F FS2 UL1066
| SPD 1400 s | 65000 | WL 3200 S,H FS2 UL1066
| SPD 1400 s | 85000 | WL 3200 L FS2 UL1066
| SPD 1400 s | 100000 | WL 3200 M FS3 UL1066
| SPD 1400 s | 40000 | WL 3200 F FS3 UL1066
| SPD 1400 s | 85000 | WL 4000 H FS3 UL1066
| SPD 1400 s | 100000 | WL 4000 L,M FS3 UL1066
| SPD 1400 s | 40000 | WL 4000 F FS3 UL1066
| SPD 1400 s | 85000 | WL 5000 H FS3 UL1066
| SPD 1400 s | 100000 | WL 5000 L,M FS3 UL1066
| SPD 1400 s | 40000 | WL 5000 F FS3 UL1066
| SPD 1600 s | 52000 | WL 2000 FS2 UL489
| SPD 1600 s | 52000 | WL 2500 FS2 UL489
| SPD 1600 s | 52000 | WL 3000 FS2 UL489
| SPD 1600 s | 68000 | WL 4000 FS3 UL489
| SPD 1600 s | 68000 | WL 5000 FS3 UL489
| SPD 1600 s | 65000 | WL 2000 S,H FS2 UL1066
| SPD 1600 s | 85000 | WL 2000 L FS2 UL1066
| SPD 1600 s | 20000 | WL 2000 F FS2 UL1066
| SPD 1600 s | 65000 | WL 3200 S,H FS2 UL1066
| SPD 1600 s | 85000 | WL 3200 L FS2 UL1066
| SPD 1600 s | 100000 | WL 3200 M FS3 UL1066
| SPD 1600 s | 40000 | WL 3200 F FS3 UL1066
| SPD 1600 s | 85000 | WL 4000 H FS3 UL1066
| SPD 1600 s | 100000 | WL 4000 L,M FS3 UL1066
| SPD 1600 s | 40000 | WL 4000 F FS3 UL1066
| SPD 1600 s | 85000 | WL 5000 H FS3 UL1066
| SPD 1600 s | 100000 | WL 5000 L,M FS3 UL1066
| SPD 1600 s | 40000 | WL 5000 F FS3 UL1066
| PG 1200 s | 52000 | WL 1600 FS2 UL489
| PG 1200 s | 52000 | WL 2000 FS2 UL489
| PG 1200 s | 52000 | WL 2500 FS2 UL489
| PG 1200 s | 52000 | WL 3000 FS2 UL489
| PG 1200 s | 68000 | WL 4000 FS3 UL489
| PG 1200 s | 68000 | WL 5000 FS3 UL489
| PG 1200 s | 50000 | WL 1600 N FS2 UL1066
| PG 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 1600 L FS2 UL1066
| PG 1200 s | 20000 | WL 1600 F FS2 UL1066
| PG 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 2000 L FS2 UL1066
| PG 1200 s | 20000 | WL 2000 F FS2 UL1066
| PG 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 3200 L FS2 UL1066
| PG 1200 s | 100000 | WL 3200 M FS3 UL1066
| PG 1200 s | 40000 | WL 3200 F FS3 UL1066
| PG 1200 s | 85000 | WL 4000 H FS3 UL1066
| PG 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| PG 1200 s | 40000 | WL 4000 F FS3 UL1066
| PG 1200 s | 85000 | WL 5000 H FS3 UL1066
| PG 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| PG 1200 s | 40000 | WL 5000 F FS3 UL1066
| PG 1600 s | 52000 | WL 2500 FS2 UL489
| PG 1600 s | 52000 | WL 3000 FS2 UL489
| PG 1600 s | 68000 | WL 4000 FS3 UL489
| PG 1600 s | 68000 | WL 5000 FS3 UL489
| PG 1600 s | 65000 | WL 3200 S,H FS2 UL1066
| PG 1600 s | 85000 | WL 3200 L FS2 UL1066
| PG 1600 s | 100000 | WL 3200 M FS3 UL1066
| PG 1600 s | 40000 | WL 3200 F FS3 UL1066
| PG 1600 s | 85000 | WL 4000 H FS3 UL1066
| PG 1600 s | 100000 | WL 4000 L,M FS3 UL1066
| PG 1600 s | 40000 | WL 4000 F FS3 UL1066
| PG 1600 s | 85000 | WL 5000 H FS3 UL1066
| PG 1600 s | 100000 | WL 5000 L,M FS3 UL1066
| PG 1600 s | 40000 | WL 5000 F FS3 UL1066
| WL 800 FS1 UL489 | 52000 | WL 1200 FS1 UL489
| WL 800 FS1 UL489 | 52000 | WL 1200 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 1600 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 2000 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 2500 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 3000 FS2 UL489
| WL 800 FS1 UL489 | 68000 | WL 4000 FS3 UL489
| WL 800 FS1 UL489 | 68000 | WL 5000 FS3 UL489
| WL 800 FS1 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 800 FS1 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 800 FS1 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 800 FS1 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 800 FS1 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 800 FS1 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 800 FS1 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 800 FS1 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1200 FS1 UL489 | 52000 | WL 1600 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1200 FS1 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1200 FS1 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1200 FS1 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 1200 FS1 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1200 FS1 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 800 FS2 UL489 | 52000 | WL 1200 FS1 UL489
| WL 800 FS2 UL489 | 52000 | WL 1200 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 1600 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 800 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 800 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 800 FS2 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 800 FS2 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 800 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 800 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 800 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 800 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 800 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 800 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1200 FS2 UL489 | 52000 | WL 1600 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1200 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1200 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1200 FS2 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 1200 FS2 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1200 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1600 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1600 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1600 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1600 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1600 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 2000 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 2000 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 2000 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 2000 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 2500 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 2500 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 2500 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 2500 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 3000 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 3000 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 3000 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 3000 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3000 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 3000 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 3000 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3000 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 FS3 UL489 | 68000 | WL 5000 FS3 UL489
| WL 4000 FS3 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 FS3 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 FS3 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 5000 FS3 UL489 |  | na
| WL 800 N FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 N FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 N FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 N FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 N FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 N FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 S,H FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 L FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 L FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 L FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 L FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 F FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 F FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 F FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 N FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 N FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 N FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 N FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 N FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 N FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 N FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 L FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 L FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 F FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 M FS3 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 M FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 M FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 M FS3 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 M FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 M FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 M FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 M FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 F FS3 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 F FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 F FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 F FS3 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 F FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 F FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 F FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 H FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 H FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 H FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 H FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 L,M FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 F FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 F FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 F FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 5000 H FS3 UL1066 |  | na
| WL 5000 L,M FS3 UL1066 |  | na
| WL 5000 F FS3 UL1066 |  | na

## 240V Selectively Coord. Pairs (hidden)
240V Selectively Coordinated Pairs
| Column1 |  | Column1 | Column1
| BQD 20 | 625 | BQD 100 | BQD 20 | None |  | None |  | None |  | BQD 100 | 625 | BQD 100 | 625
| BQD 20 | 590 | ED 60 | BQD 100 | BQD 100 | 625 | BQD 100 | 625 | BQD 100 | 625 | ED 60 | 590 | ED 60 | 590
| BQD 20 | 880 | ED 100 | BL 20 | ED 60 | 590 | ED 60 | 590 | ED 60 | 590 | ED 100 | 880 | ED 100 | 880
| BQD 20 | 1000 | ED 125 | ED 60 | ED 100 | 880 | ED 100 | 880 | ED 100 | 880 | ED 125 | 1000 | ED 125 | 1000
| BQD 20 | 960 | FD 100 | ED 100 | ED 125 | 1000 | ED 125 | 1000 | ED 125 | 1000 | FD 100 | 960 | FD 100 | 960
| BQD 20 | 1200 | FD 150 | ED 125 | FD 100 | 960 | FD 100 | 960 | FD 100 | 960 | FD 150 | 1200 | FD 150 | 1200
| BQD 20 | 1600 | FD 200 | FD 100 | FD 150 | 1200 | FD 150 | 1200 | FD 150 | 1200 | FD 200 | 1600 | FD 200 | 1600
| BQD 20 | 1950 | FD 250 | FD 150 | FD 200 | 1600 | FD 200 | 1600 | FD 200 | 1600 | FD 250 | 1950 | FD 250 | 1950
| BQD 20 | 1950 | JD 300 | FD 200 | FD 250 | 1950 | FD 250 | 1950 | FD 250 | 1950 | JD 300 | 1950 | JD 300 | 1950
| BQD 20 | 3200 | JD 400 | FD 250 | JD 300 | 1950 | JD 300 | 1950 | JD 300 | 1950 | JD 400 | 3200 | JD 400 | 3200
| BQD 20 | 2000 | SJD 200 s | JD 300 | JD 400 | 3200 | JD 400 | 3200 | JD 400 | 3200 | SJD 200 s | 2000 | SJD 200 s | 2000
| BQD 20 | 3100 | SJD 300 s | JD 400 | SJD 200 s | 2000 | SJD 200 s | 2000 | SJD 200 s | 2000 | SJD 300 s | 3100 | SJD 300 s | 3100
| BQD 20 | 4200 | SJD 400 s | SJD 200 s | SJD 300 s | 3100 | SJD 300 s | 3100 | SJD 300 s | 3100 | SJD 400 s | 4200 | SJD 400 s | 4200
| BQD 20 | 1980 | LD 250 | SJD 300 s | SJD 400 s | 4200 | SJD 400 s | 4200 | SJD 400 s | 4200 | LD 250 | 1980 | LD 250 | 1980
| BQD 20 | 3200 | LD 400 | SJD 400 s | LD 250 | 1980 | LD 250 | 1980 | LD 250 | 1980 | LD 400 | 3200 | LD 400 | 3200
| BQD 20 | 4800 | LD 500 | LD 250 | LD 400 | 3200 | LD 400 | 3200 | LD 400 | 3200 | LD 500 | 4800 | LD 500 | 4800
| BQD 20 | 4800 | LD 600 | LD 400 | LD 500 | 4800 | LD 500 | 4800 | LD 500 | 4800 | LD 600 | 4800 | LD 600 | 4800
| BQD 20 | 3100 | SLD 300 s | LD 500 | LD 600 | 4800 | LD 600 | 4800 | LD 600 | 4800 | SLD 300 s | 3100 | SLD 300 s | 3100
| BQD 20 | 4100 | SLD 400 s | LD 600 | SLD 300 s | 3100 | SLD 300 s | 3100 | SLD 300 s | 3100 | SLD 400 s | 4100 | SLD 400 s | 4100
| BQD 20 | 5200 | SLD 500 s | SLD 300 s | SLD 400 s | 4100 | SLD 400 s | 4100 | SLD 400 s | 4100 | SLD 500 s | 5200 | SLD 500 s | 5200
| BQD 20 | 6200 | SLD 600 s | SLD 400 s | SLD 500 s | 5200 | SLD 500 s | 5200 | SLD 500 s | 5200 | SLD 600 s | 6200 | SLD 600 s | 6200
| BQD 20 | 5000 | MD 500 | SLD 500 s | SLD 600 s | 6200 | SLD 600 s | 6200 | SLD 600 s | 6200 | MD 500 | 5000 | MD 500 | 5000
| BQD 20 | 6500 | MD 600 | SLD 600 s | MD 500 | 5000 | MD 500 | 5000 | MD 500 | 5000 | MD 600 | 6500 | MD 600 | 6500
| BQD 20 | 6500 | MD 800 | MD 500 | MD 600 | 6500 | MD 600 | 6500 | MD 600 | 6500 | MD 800 | 6500 | MD 800 | 6500
| BQD 20 | 4800 | MG 600 | MD 600 | MD 800 | 6500 | MD 800 | 6500 | MD 800 | 6500 | MG 600 | 4800 | MG 600 | 4800
| BQD 20 | 5200 | MG 800 | MD 800 | MG 600 | 4800 | MG 600 | 4800 | MG 600 | 4800 | MG 800 | 5200 | MG 800 | 5200
| BQD 20 | 7200 | SMD 600 s | MG 600 | MG 800 | 5200 | MG 800 | 5200 | MG 800 | 5200 | SMD 600 s | 7200 | SMD 600 s | 7200
| BQD 20 | 9600 | SMD 800 s | MG 800 | SMD 600 s | 7200 | SMD 600 s | 7200 | SMD 600 s | 7200 | SMD 800 s | 9600 | SMD 800 s | 9600
| BQD 20 | 4800 | MG 600 s | SMD 600 s | SMD 800 s | 9600 | SMD 800 s | 9600 | SMD 800 s | 9600 | MG 600 s | 4800 | MG 600 s | 4800
| BQD 20 | 4800 | MG 800 s | SMD 800 s | MG 600 s | 4800 | MG 600 s | 4800 | MG 600 s | 4800 | MG 800 s | 4800 | MG 800 s | 4800
| BQD 20 | 8000 | ND 1000 | MG 600 s | MG 800 s | 4800 | MG 800 s | 4800 | MG 800 s | 4800 | ND 1000 | 8000 | ND 1000 | 8000
| BQD 20 | 8000 | ND 1200 | MG 800 s | ND 1000 | 8000 | ND 1000 | 8000 | ND 1000 | 8000 | ND 1200 | 8000 | ND 1200 | 8000
| BQD 20 | 6400 | NG 800 | ND 1000 | ND 1200 | 8000 | ND 1200 | 8000 | ND 1200 | 8000 | NG 800 | 6400 | NG 800 | 6400
| BQD 20 | 8000 | NG 1000 | ND 1200 | NG 800 | 6400 | NG 800 | 6400 | NG 800 | 6400 | NG 1000 | 8000 | NG 1000 | 8000
| BQD 20 | 9600 | NG 1200 | NG 800 | NG 1000 | 8000 | NG 1000 | 8000 | NG 1000 | 8000 | NG 1200 | 9600 | NG 1200 | 9600
| BQD 20 | 9400 | SND 800 s | NG 1000 | NG 1200 | 9600 | NG 1200 | 9600 | NG 1200 | 9600 | SND 800 s | 9400 | SND 800 s | 9400
| BQD 20 | 10000 | SND 1000 s | NG 1200 | SND 800 s | 9400 | SND 800 s | 9400 | SND 800 s | 9400 | SND 1000 s | 10000 | SND 1000 s | 10000
| BQD 20 | 10000 | SND 1200 s | SND 800 s | SND 1000 s | 10000 | SND 1000 s | 10000 | SND 1000 s | 10000 | SND 1200 s | 10000 | SND 1200 s | 10000
| BQD 20 | 7040 | NG 800 s | SND 1000 s | SND 1200 s | 10000 | SND 1200 s | 10000 | SND 1200 s | 10000 | NG 800 s | 7040 | NG 800 s | 7040
| BQD 20 | 8800 | NG 1000 s | SND 1200 s | NG 800 s | 7040 | NG 800 s | 7040 | NG 800 s | 7040 | NG 1000 s | 8800 | NG 1000 s | 8800
| BQD 20 | 9600 | NG 1200 s | NG 800 s | NG 1000 s | 8800 | NG 1000 s | 8800 | NG 1000 s | 8800 | NG 1200 s | 9600 | NG 1200 s | 9600
| BQD 20 | 8000 | PD 1200 | NG 1000 s | NG 1200 s | 9600 | NG 1200 s | 9600 | NG 1200 s | 9600 | PD 1200 | 8000 | PD 1200 | 8000
| BQD 20 | 8000 | PD 1600 | NG 1200 s | PD 1200 | 8000 | PD 1200 | 8000 | PD 1200 | 8000 | PD 1600 | 8000 | PD 1600 | 8000
| BQD 20 | 9600 | PG 1200 | PD 1200 | PD 1600 | 8000 | PD 1600 | 8000 | PD 1600 | 8000 | PG 1200 | 9600 | PG 1200 | 9600
| BQD 20 | 9600 | PG 1600 | PD 1600 | PG 1200 | 9600 | PG 1200 | 9600 | PG 1200 | 9600 | PG 1600 | 9600 | PG 1600 | 9600
| BQD 20 | 10000 | SPD 1400 s | PG 1200 | PG 1600 | 9600 | PG 1600 | 9600 | PG 1600 | 9600 | SPD 1400 s | 10000 | SPD 1400 s | 10000
| BQD 20 | 10000 | SPD 1600 s | PG 1600 | SPD 1400 s | 10000 | SPD 1400 s | 10000 | SPD 1400 s | 10000 | SPD 1600 s | 10000 | SPD 1600 s | 10000
| BQD 20 | 9600 | PG 1200 s | SPD 1400 s | SPD 1600 s | 10000 | SPD 1600 s | 10000 | SPD 1600 s | 10000 | PG 1200 s | 9600 | PG 1200 s | 9600
| BQD 20 | 7680 | PG 1600 s | SPD 1600 s | PG 1200 s | 9600 | PG 1200 s | 9600 | PG 1200 s | 9600 | PG 1600 s | 7680 | PG 1600 s | 7680
| BQD 20 | 52000 | WL 800 FS1 UL489 | PG 1200 s | PG 1600 s | 7680 | PG 1600 s | 7680 | PG 1600 s | 7680 | WL 800 FS1 UL489 | 52000 | WL 800 FS1 UL489 | 52000
| BQD 20 | 52000 | WL 1200 FS1 UL489 | PG 1600 s | WL 800 FS1 UL489 | 52000 | WL 800 FS1 UL489 | 52000 | WL 800 FS1 UL489 | 52000 | WL 1200 FS1 UL489 | 52000 | WL 1200 FS1 UL489 | 52000
| BQD 20 | 52000 | WL 800 FS2 UL489 | WL 800 FS1 UL489 | WL 1200 FS1 UL489 | 52000 | WL 1200 FS1 UL489 | 52000 | WL 1200 FS1 UL489 | 52000 | WL 800 FS2 UL489 | 52000 | WL 800 FS2 UL489 | 52000
| BQD 20 | 52000 | WL 1200 FS2 UL489 | WL 1200 FS1 UL489 | WL 800 FS2 UL489 | 52000 | WL 800 FS2 UL489 | 52000 | WL 800 FS2 UL489 | 52000 | WL 1200 FS2 UL489 | 52000 | WL 1200 FS2 UL489 | 52000
| BQD 20 | 52000 | WL 1600 FS2 UL489 | WL 800 FS2 UL489 | WL 1200 FS2 UL489 | 52000 | WL 1200 FS2 UL489 | 52000 | WL 1200 FS2 UL489 | 52000 | WL 1600 FS2 UL489 | 52000 | WL 1600 FS2 UL489 | 52000
| BQD 20 | 52000 | WL 2000 FS2 UL489 | WL 1200 FS2 UL489 | WL 1600 FS2 UL489 | 52000 | WL 1600 FS2 UL489 | 52000 | WL 1600 FS2 UL489 | 52000 | WL 2000 FS2 UL489 | 52000 | WL 2000 FS2 UL489 | 52000
| BQD 20 | 52000 | WL 2500 FS2 UL489 | WL 1600 FS2 UL489 | WL 2000 FS2 UL489 | 52000 | WL 2000 FS2 UL489 | 52000 | WL 2000 FS2 UL489 | 52000 | WL 2500 FS2 UL489 | 52000 | WL 2500 FS2 UL489 | 52000
| BQD 20 | 52000 | WL 3000 FS2 UL489 | WL 2000 FS2 UL489 | WL 2500 FS2 UL489 | 52000 | WL 2500 FS2 UL489 | 52000 | WL 2500 FS2 UL489 | 52000 | WL 3000 FS2 UL489 | 52000 | WL 3000 FS2 UL489 | 52000
| BQD 20 | 50000 | WL 800 N FS2 UL1066 | WL 2500 FS2 UL489 | WL 3000 FS2 UL489 | 52000 | WL 3000 FS2 UL489 | 52000 | WL 3000 FS2 UL489 | 52000 | WL 800 N FS2 UL1066 | 50000 | WL 800 N FS2 UL1066 | 50000
| BQD 20 | 65000 | WL 800 S,H FS2 UL1066 | WL 3000 FS2 UL489 | WL 800 N FS2 UL1066 | 50000 | WL 800 N FS2 UL1066 | 50000 | WL 800 N FS2 UL1066 | 50000 | WL 800 S,H FS2 UL1066 | 65000 | WL 800 S,H FS2 UL1066 | 65000
| BQD 20 | 20000 | WL 800 F FS2 UL1066 | WL 4000 FS3 UL489 | WL 800 S,H FS2 UL1066 | 65000 | WL 800 S,H FS2 UL1066 | 65000 | WL 800 S,H FS2 UL1066 | 65000 | WL 800 F FS2 UL1066 | 20000 | WL 800 F FS2 UL1066 | 20000
| BQD 20 | 50000 | WL 1600 N FS2 UL1066 | WL 5000 FS3 UL489 | WL 800 F FS2 UL1066 | 20000 | WL 800 F FS2 UL1066 | 20000 | WL 800 F FS2 UL1066 | 20000 | WL 1600 N FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066 | 50000
| BQD 20 | 65000 | WL 1600 S,H FS2 UL1066 | WL 800 N FS2 UL1066 | WL 1600 N FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066 | 50000 | WL 1600 S,H FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066 | 65000
| BQD 20 | 20000 | WL 1600 F FS2 UL1066 | WL 800 S,H FS2 UL1066 | WL 1600 S,H FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066 | 65000 | WL 1600 F FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066 | 20000
| BQD 20 | 65000 | WL 2000 S,H FS2 UL1066 | WL 800 L FS2 UL1066 | WL 1600 F FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066 | 20000 | WL 2000 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066 | 65000
| BQD 20 | 20000 | WL 2000 F FS2 UL1066 | WL 800 F FS2 UL1066 | WL 2000 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066 | 65000 | WL 2000 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066 | 20000
| BQD 20 | 65000 | WL 3200 S,H FS2 UL1066 | WL 1600 N FS2 UL1066 | WL 2000 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066 | 20000 | WL 3200 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066 | 65000
| BQD 20 | 40000 | WL 3200 F FS3 UL1066 | WL 1600 S,H FS2 UL1066 | WL 3200 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066 | 65000 | WL 3200 F FS3 UL1066 | 40000 | WL 3200 F FS3 UL1066 | 40000
| BQD 20 | 85000 | WL 4000 H FS3 UL1066 | WL 1600 L FS2 UL1066 | WL 3200 F FS3 UL1066 | 40000 | WL 3200 F FS3 UL1066 | 40000 | WL 3200 F FS3 UL1066 | 40000 | WL 4000 H FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066 | 85000
| BQD 20 | 40000 | WL 4000 F FS3 UL1066 | WL 1600 F FS2 UL1066 | WL 4000 H FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066 | 85000 | WL 4000 F FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066 | 40000
| BQD 20 | 40000 | WL 5000 F FS3 UL1066 | WL 2000 S,H FS2 UL1066 | WL 4000 F FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066 | 40000
| BQD 100 | 1200 | FD 150 | WL 2000 L FS2 UL1066 | WL 5000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066 | 40000
| BQD 100 | 1600 | FD 200 | WL 2000 F FS2 UL1066
| BQD 100 | 1950 | FD 250 | WL 3200 S,H FS2 UL1066
| BQD 100 | 1950 | JD 300 | WL 3200 L FS2 UL1066
| BQD 100 | 3200 | JD 400 | WL 3200 M FS3 UL1066
| BQD 100 | 2000 | SJD 200 s | WL 3200 F FS3 UL1066
| BQD 100 | 3100 | SJD 300 s | WL 4000 H FS3 UL1066
| BQD 100 | 4200 | SJD 400 s | WL 4000 L,M FS3 UL1066
| BQD 100 | 1980 | LD 250 | WL 4000 F FS3 UL1066
| BQD 100 | 3200 | LD 400 | WL 5000 H FS3 UL1066
| BQD 100 | 4800 | LD 500 | WL 5000 L,M FS3 UL1066
| BQD 100 | 4800 | LD 600 | WL 5000 F FS3 UL1066
| BQD 100 | 3100 | SLD 300 s
| BQD 100 | 4100 | SLD 400 s
| BQD 100 | 5200 | SLD 500 s
| BQD 100 | 6200 | SLD 600 s
| BQD 100 | 5000 | MD 500
| BQD 100 | 6500 | MD 600
| BQD 100 | 6500 | MD 800
| BQD 100 | 4800 | MG 600
| BQD 100 | 5200 | MG 800
| BQD 100 | 7200 | SMD 600 s
| BQD 100 | 9600 | SMD 800 s
| BQD 100 | 4800 | MG 600 s
| BQD 100 | 4800 | MG 800 s
| BQD 100 | 8000 | ND 1000
| BQD 100 | 8000 | ND 1200
| BQD 100 | 6400 | NG 800
| BQD 100 | 8000 | NG 1000
| BQD 100 | 9600 | NG 1200
| BQD 100 | 9400 | SND 800 s
| BQD 100 | 10000 | SND 1000 s
| BQD 100 | 10000 | SND 1200 s
| BQD 100 | 7040 | NG 800 s
| BQD 100 | 8800 | NG 1000 s
| BQD 100 | 9600 | NG 1200 s
| BQD 100 | 8000 | PD 1200
| BQD 100 | 8000 | PD 1600
| BQD 100 | 9600 | PG 1200
| BQD 100 | 9600 | PG 1600
| BQD 100 | 10000 | SPD 1400 s
| BQD 100 | 10000 | SPD 1600 s
| BQD 100 | 9600 | PG 1200 s
| BQD 100 | 7680 | PG 1600 s
| BQD 100 | 52000 | WL 800 FS1 UL489
| BQD 100 | 52000 | WL 1200 FS1 UL489
| BQD 100 | 52000 | WL 800 FS2 UL489
| BQD 100 | 52000 | WL 1200 FS2 UL489
| BQD 100 | 52000 | WL 1600 FS2 UL489
| BQD 100 | 52000 | WL 2000 FS2 UL489
| BQD 100 | 52000 | WL 2500 FS2 UL489
| BQD 100 | 52000 | WL 3000 FS2 UL489
| BQD 100 | 65000 | WL 4000 FS3 UL489
| BQD 100 | 65000 | WL 5000 FS3 UL489
| BQD 100 | 50000 | WL 800 N FS2 UL1066
| BQD 100 | 65000 | WL 800 S,H FS2 UL1066
| BQD 100 | 65000 | WL 800 L FS2 UL1066
| BQD 100 | 20000 | WL 800 F FS2 UL1066
| BQD 100 | 50000 | WL 1600 N FS2 UL1066
| BQD 100 | 65000 | WL 1600 S,H FS2 UL1066
| BQD 100 | 65000 | WL 1600 L FS2 UL1066
| BQD 100 | 20000 | WL 1600 F FS2 UL1066
| BQD 100 | 65000 | WL 2000 S,H FS2 UL1066
| BQD 100 | 65000 | WL 2000 L FS2 UL1066
| BQD 100 | 20000 | WL 2000 F FS2 UL1066
| BQD 100 | 65000 | WL 3200 S,H FS2 UL1066
| BQD 100 | 65000 | WL 3200 L FS2 UL1066
| BQD 100 | 65000 | WL 3200 M FS3 UL1066
| BQD 100 | 40000 | WL 3200 F FS3 UL1066
| BQD 100 | 65000 | WL 4000 H FS3 UL1066
| BQD 100 | 65000 | WL 4000 L,M FS3 UL1066
| BQD 100 | 40000 | WL 4000 F FS3 UL1066
| BQD 100 | 65000 | WL 5000 H FS3 UL1066
| BQD 100 | 65000 | WL 5000 L,M FS3 UL1066
| BQD 100 | 40000 | WL 5000 F FS3 UL1066
| BL 20 | 625 | BQD 100
| BL 20 | 590 | ED 60
| BL 20 | 880 | ED 100
| BL 20 | 1000 | ED 125
| BL 20 | 960 | FD 100
| BL 20 | 1200 | FD 150
| BL 20 | 1600 | FD 200
| BL 20 | 1950 | FD 250
| BL 20 | 1950 | JD 300
| BL 20 | 3200 | JD 400
| BL 20 | 2000 | SJD 200 s
| BL 20 | 3100 | SJD 300 s
| BL 20 | 4200 | SJD 400 s
| BL 20 | 1980 | LD 250
| BL 20 | 3200 | LD 400
| BL 20 | 4800 | LD 500
| BL 20 | 4800 | LD 600
| BL 20 | 3100 | SLD 300 s
| BL 20 | 4100 | SLD 400 s
| BL 20 | 5200 | SLD 500 s
| BL 20 | 6200 | SLD 600 s
| BL 20 | 5000 | MD 500
| BL 20 | 6500 | MD 600
| BL 20 | 6500 | MD 800
| BL 20 | 4800 | MG 600
| BL 20 | 5200 | MG 800
| BL 20 | 7200 | SMD 600 s
| BL 20 | 9600 | SMD 800 s
| BL 20 | 4800 | MG 600 s
| BL 20 | 4800 | MG 800 s
| BL 20 | 8000 | ND 1000
| BL 20 | 8000 | ND 1200
| BL 20 | 6400 | NG 800
| BL 20 | 8000 | NG 1000
| BL 20 | 9600 | NG 1200
| BL 20 | 9400 | SND 800 s
| BL 20 | 10000 | SND 1000 s
| BL 20 | 10000 | SND 1200 s
| BL 20 | 7040 | NG 800 s
| BL 20 | 8800 | NG 1000 s
| BL 20 | 9600 | NG 1200 s
| BL 20 | 8000 | PD 1200
| BL 20 | 8000 | PD 1600
| BL 20 | 9600 | PG 1200
| BL 20 | 9600 | PG 1600
| BL 20 | 10000 | SPD 1400 s
| BL 20 | 10000 | SPD 1600 s
| BL 20 | 9600 | PG 1200 s
| BL 20 | 7680 | PG 1600 s
| BL 20 | 52000 | WL 800 FS1 UL489
| BL 20 | 52000 | WL 1200 FS1 UL489
| BL 20 | 52000 | WL 800 FS2 UL489
| BL 20 | 52000 | WL 1200 FS2 UL489
| BL 20 | 52000 | WL 1600 FS2 UL489
| BL 20 | 52000 | WL 2000 FS2 UL489
| BL 20 | 52000 | WL 2500 FS2 UL489
| BL 20 | 52000 | WL 3000 FS2 UL489
| BL 20 | 50000 | WL 800 N FS2 UL1066
| BL 20 | 65000 | WL 800 S,H FS2 UL1066
| BL 20 | 20000 | WL 800 F FS2 UL1066
| BL 20 | 50000 | WL 1600 N FS2 UL1066
| BL 20 | 65000 | WL 1600 S,H FS2 UL1066
| BL 20 | 20000 | WL 1600 F FS2 UL1066
| BL 20 | 65000 | WL 2000 S,H FS2 UL1066
| BL 20 | 20000 | WL 2000 F FS2 UL1066
| BL 20 | 65000 | WL 3200 S,H FS2 UL1066
| BL 20 | 40000 | WL 3200 F FS3 UL1066
| BL 20 | 40000 | WL 4000 F FS3 UL1066
| BL 20 | 40000 | WL 5000 F FS3 UL1066
| ED 60 | 960 | FD 100
| ED 60 | 1200 | FD 150
| ED 60 | 1600 | FD 200
| ED 60 | 1950 | FD 250
| ED 60 | 1950 | JD 300
| ED 60 | 3200 | JD 400
| ED 60 | 2000 | SJD 200 s
| ED 60 | 3100 | SJD 300 s
| ED 60 | 4200 | SJD 400 s
| ED 60 | 1980 | LD 250
| ED 60 | 3200 | LD 400
| ED 60 | 4800 | LD 500
| ED 60 | 4800 | LD 600
| ED 60 | 3100 | SLD 300 s
| ED 60 | 4100 | SLD 400 s
| ED 60 | 5200 | SLD 500 s
| ED 60 | 6200 | SLD 600 s
| ED 60 | 5000 | MD 500
| ED 60 | 6500 | MD 600
| ED 60 | 6500 | MD 800
| ED 60 | 4800 | MG 600
| ED 60 | 5200 | MG 800
| ED 60 | 7200 | SMD 600 s
| ED 60 | 9600 | SMD 800 s
| ED 60 | 4800 | MG 600 s
| ED 60 | 4800 | MG 800 s
| ED 60 | 8000 | ND 1000
| ED 60 | 8000 | ND 1200
| ED 60 | 6400 | NG 800
| ED 60 | 8000 | NG 1000
| ED 60 | 9600 | NG 1200
| ED 60 | 9400 | SND 800 s
| ED 60 | 10000 | SND 1000 s
| ED 60 | 10000 | SND 1200 s
| ED 60 | 7040 | NG 800 s
| ED 60 | 8800 | NG 1000 s
| ED 60 | 9600 | NG 1200 s
| ED 60 | 8000 | PD 1200
| ED 60 | 8000 | PD 1600
| ED 60 | 9600 | PG 1200
| ED 60 | 9600 | PG 1600
| ED 60 | 10000 | SPD 1400 s
| ED 60 | 10000 | SPD 1600 s
| ED 60 | 9600 | PG 1200 s
| ED 60 | 7680 | PG 1600 s
| ED 60 | 52000 | WL 800 FS1 UL489
| ED 60 | 52000 | WL 1200 FS1 UL489
| ED 60 | 52000 | WL 800 FS2 UL489
| ED 60 | 52000 | WL 1200 FS2 UL489
| ED 60 | 52000 | WL 1600 FS2 UL489
| ED 60 | 52000 | WL 2000 FS2 UL489
| ED 60 | 52000 | WL 2500 FS2 UL489
| ED 60 | 52000 | WL 3000 FS2 UL489
| ED 60 | 68000 | WL 4000 FS3 UL489
| ED 60 | 68000 | WL 5000 FS3 UL489
| ED 60 | 50000 | WL 800 N FS2 UL1066
| ED 60 | 65000 | WL 800 S,H FS2 UL1066
| ED 60 | 85000 | WL 800 L FS2 UL1066
| ED 60 | 20000 | WL 800 F FS2 UL1066
| ED 60 | 50000 | WL 1600 N FS2 UL1066
| ED 60 | 65000 | WL 1600 S,H FS2 UL1066
| ED 60 | 85000 | WL 1600 L FS2 UL1066
| ED 60 | 20000 | WL 1600 F FS2 UL1066
| ED 60 | 65000 | WL 2000 S,H FS2 UL1066
| ED 60 | 85000 | WL 2000 L FS2 UL1066
| ED 60 | 20000 | WL 2000 F FS2 UL1066
| ED 60 | 65000 | WL 3200 S,H FS2 UL1066
| ED 60 | 85000 | WL 3200 L FS2 UL1066
| ED 60 | 100000 | WL 3200 M FS3 UL1066
| ED 60 | 40000 | WL 3200 F FS3 UL1066
| ED 60 | 85000 | WL 4000 H FS3 UL1066
| ED 60 | 100000 | WL 4000 L,M FS3 UL1066
| ED 60 | 40000 | WL 4000 F FS3 UL1066
| ED 60 | 85000 | WL 5000 H FS3 UL1066
| ED 60 | 100000 | WL 5000 L,M FS3 UL1066
| ED 60 | 40000 | WL 5000 F FS3 UL1066
| ED 100 | 1200 | FD 150
| ED 100 | 1600 | FD 200
| ED 100 | 1950 | FD 250
| ED 100 | 1950 | JD 300
| ED 100 | 3200 | JD 400
| ED 100 | 2000 | SJD 200 s
| ED 100 | 3100 | SJD 300 s
| ED 100 | 4200 | SJD 400 s
| ED 100 | 1980 | LD 250
| ED 100 | 3200 | LD 400
| ED 100 | 4800 | LD 500
| ED 100 | 4800 | LD 600
| ED 100 | 3100 | SLD 300 s
| ED 100 | 4100 | SLD 400 s
| ED 100 | 5200 | SLD 500 s
| ED 100 | 6200 | SLD 600 s
| ED 100 | 5000 | MD 500
| ED 100 | 6500 | MD 600
| ED 100 | 6500 | MD 800
| ED 100 | 4800 | MG 600
| ED 100 | 5200 | MG 800
| ED 100 | 7200 | SMD 600 s
| ED 100 | 9600 | SMD 800 s
| ED 100 | 4800 | MG 600 s
| ED 100 | 4800 | MG 800 s
| ED 100 | 8000 | ND 1000
| ED 100 | 8000 | ND 1200
| ED 100 | 6400 | NG 800
| ED 100 | 8000 | NG 1000
| ED 100 | 9600 | NG 1200
| ED 100 | 9400 | SND 800 s
| ED 100 | 10000 | SND 1000 s
| ED 100 | 10000 | SND 1200 s
| ED 100 | 7040 | NG 800 s
| ED 100 | 8800 | NG 1000 s
| ED 100 | 9600 | NG 1200 s
| ED 100 | 8000 | PD 1200
| ED 100 | 8000 | PD 1600
| ED 100 | 9600 | PG 1200
| ED 100 | 9600 | PG 1600
| ED 100 | 10000 | SPD 1400 s
| ED 100 | 10000 | SPD 1600 s
| ED 100 | 9600 | PG 1200 s
| ED 100 | 7680 | PG 1600 s
| ED 100 | 52000 | WL 800 FS1 UL489
| ED 100 | 52000 | WL 1200 FS1 UL489
| ED 100 | 52000 | WL 800 FS2 UL489
| ED 100 | 52000 | WL 1200 FS2 UL489
| ED 100 | 52000 | WL 1600 FS2 UL489
| ED 100 | 52000 | WL 2000 FS2 UL489
| ED 100 | 52000 | WL 2500 FS2 UL489
| ED 100 | 52000 | WL 3000 FS2 UL489
| ED 100 | 68000 | WL 4000 FS3 UL489
| ED 100 | 68000 | WL 5000 FS3 UL489
| ED 100 | 50000 | WL 800 N FS2 UL1066
| ED 100 | 65000 | WL 800 S,H FS2 UL1066
| ED 100 | 85000 | WL 800 L FS2 UL1066
| ED 100 | 20000 | WL 800 F FS2 UL1066
| ED 100 | 50000 | WL 1600 N FS2 UL1066
| ED 100 | 65000 | WL 1600 S,H FS2 UL1066
| ED 100 | 85000 | WL 1600 L FS2 UL1066
| ED 100 | 20000 | WL 1600 F FS2 UL1066
| ED 100 | 65000 | WL 2000 S,H FS2 UL1066
| ED 100 | 85000 | WL 2000 L FS2 UL1066
| ED 100 | 20000 | WL 2000 F FS2 UL1066
| ED 100 | 65000 | WL 3200 S,H FS2 UL1066
| ED 100 | 85000 | WL 3200 L FS2 UL1066
| ED 100 | 100000 | WL 3200 M FS3 UL1066
| ED 100 | 40000 | WL 3200 F FS3 UL1066
| ED 100 | 85000 | WL 4000 H FS3 UL1066
| ED 100 | 100000 | WL 4000 L,M FS3 UL1066
| ED 100 | 40000 | WL 4000 F FS3 UL1066
| ED 100 | 85000 | WL 5000 H FS3 UL1066
| ED 100 | 100000 | WL 5000 L,M FS3 UL1066
| ED 100 | 40000 | WL 5000 F FS3 UL1066
| ED 125 | 1600 | FD 200
| ED 125 | 1950 | FD 250
| ED 125 | 1950 | JD 300
| ED 125 | 3200 | JD 400
| ED 125 | 2000 | SJD 200 s
| ED 125 | 3100 | SJD 300 s
| ED 125 | 4200 | SJD 400 s
| ED 125 | 1980 | LD 250
| ED 125 | 3200 | LD 400
| ED 125 | 4800 | LD 500
| ED 125 | 4800 | LD 600
| ED 125 | 3100 | SLD 300 s
| ED 125 | 4100 | SLD 400 s
| ED 125 | 5200 | SLD 500 s
| ED 125 | 6200 | SLD 600 s
| ED 125 | 5000 | MD 500
| ED 125 | 6500 | MD 600
| ED 125 | 6500 | MD 800
| ED 125 | 4800 | MG 600
| ED 125 | 5200 | MG 800
| ED 125 | 7200 | SMD 600 s
| ED 125 | 9600 | SMD 800 s
| ED 125 | 4800 | MG 600 s
| ED 125 | 4800 | MG 800 s
| ED 125 | 8000 | ND 1000
| ED 125 | 8000 | ND 1200
| ED 125 | 6400 | NG 800
| ED 125 | 8000 | NG 1000
| ED 125 | 9600 | NG 1200
| ED 125 | 9400 | SND 800 s
| ED 125 | 10000 | SND 1000 s
| ED 125 | 10000 | SND 1200 s
| ED 125 | 7040 | NG 800 s
| ED 125 | 8800 | NG 1000 s
| ED 125 | 9600 | NG 1200 s
| ED 125 | 8000 | PD 1200
| ED 125 | 8000 | PD 1600
| ED 125 | 9600 | PG 1200
| ED 125 | 9600 | PG 1600
| ED 125 | 10000 | SPD 1400 s
| ED 125 | 10000 | SPD 1600 s
| ED 125 | 9600 | PG 1200 s
| ED 125 | 7680 | PG 1600 s
| ED 125 | 52000 | WL 800 FS1 UL489
| ED 125 | 52000 | WL 1200 FS1 UL489
| ED 125 | 52000 | WL 800 FS2 UL489
| ED 125 | 52000 | WL 1200 FS2 UL489
| ED 125 | 52000 | WL 1600 FS2 UL489
| ED 125 | 52000 | WL 2000 FS2 UL489
| ED 125 | 52000 | WL 2500 FS2 UL489
| ED 125 | 52000 | WL 3000 FS2 UL489
| ED 125 | 68000 | WL 4000 FS3 UL489
| ED 125 | 68000 | WL 5000 FS3 UL489
| ED 125 | 50000 | WL 800 N FS2 UL1066
| ED 125 | 65000 | WL 800 S,H FS2 UL1066
| ED 125 | 85000 | WL 800 L FS2 UL1066
| ED 125 | 20000 | WL 800 F FS2 UL1066
| ED 125 | 50000 | WL 1600 N FS2 UL1066
| ED 125 | 65000 | WL 1600 S,H FS2 UL1066
| ED 125 | 85000 | WL 1600 L FS2 UL1066
| ED 125 | 20000 | WL 1600 F FS2 UL1066
| ED 125 | 65000 | WL 2000 S,H FS2 UL1066
| ED 125 | 85000 | WL 2000 L FS2 UL1066
| ED 125 | 20000 | WL 2000 F FS2 UL1066
| ED 125 | 65000 | WL 3200 S,H FS2 UL1066
| ED 125 | 85000 | WL 3200 L FS2 UL1066
| ED 125 | 100000 | WL 3200 M FS3 UL1066
| ED 125 | 40000 | WL 3200 F FS3 UL1066
| ED 125 | 85000 | WL 4000 H FS3 UL1066
| ED 125 | 100000 | WL 4000 L,M FS3 UL1066
| ED 125 | 40000 | WL 4000 F FS3 UL1066
| ED 125 | 85000 | WL 5000 H FS3 UL1066
| ED 125 | 100000 | WL 5000 L,M FS3 UL1066
| ED 125 | 40000 | WL 5000 F FS3 UL1066
| FD 100 | 1600 | FD 200
| FD 100 | 1950 | FD 250
| FD 100 | 1950 | JD 300
| FD 100 | 3200 | JD 400
| FD 100 | 2000 | SJD 200 s
| FD 100 | 3100 | SJD 300 s
| FD 100 | 4200 | SJD 400 s
| FD 100 | 1980 | LD 250
| FD 100 | 3200 | LD 400
| FD 100 | 4800 | LD 500
| FD 100 | 4800 | LD 600
| FD 100 | 3100 | SLD 300 s
| FD 100 | 4100 | SLD 400 s
| FD 100 | 5200 | SLD 500 s
| FD 100 | 6200 | SLD 600 s
| FD 100 | 5000 | MD 500
| FD 100 | 6500 | MD 600
| FD 100 | 6500 | MD 800
| FD 100 | 4800 | MG 600
| FD 100 | 5200 | MG 800
| FD 100 | 7200 | SMD 600 s
| FD 100 | 9600 | SMD 800 s
| FD 100 | 4800 | MG 600 s
| FD 100 | 4800 | MG 800 s
| FD 100 | 8000 | ND 1000
| FD 100 | 8000 | ND 1200
| FD 100 | 6400 | NG 800
| FD 100 | 8000 | NG 1000
| FD 100 | 9600 | NG 1200
| FD 100 | 9400 | SND 800 s
| FD 100 | 10000 | SND 1000 s
| FD 100 | 10000 | SND 1200 s
| FD 100 | 7040 | NG 800 s
| FD 100 | 8800 | NG 1000 s
| FD 100 | 9600 | NG 1200 s
| FD 100 | 8000 | PD 1200
| FD 100 | 8000 | PD 1600
| FD 100 | 9600 | PG 1200
| FD 100 | 9600 | PG 1600
| FD 100 | 10000 | SPD 1400 s
| FD 100 | 10000 | SPD 1600 s
| FD 100 | 9600 | PG 1200 s
| FD 100 | 7680 | PG 1600 s
| FD 100 | 52000 | WL 800 FS1 UL489
| FD 100 | 52000 | WL 1200 FS1 UL489
| FD 100 | 52000 | WL 800 FS2 UL489
| FD 100 | 52000 | WL 1200 FS2 UL489
| FD 100 | 52000 | WL 1600 FS2 UL489
| FD 100 | 52000 | WL 2000 FS2 UL489
| FD 100 | 52000 | WL 2500 FS2 UL489
| FD 100 | 52000 | WL 3000 FS2 UL489
| FD 100 | 68000 | WL 4000 FS3 UL489
| FD 100 | 68000 | WL 5000 FS3 UL489
| FD 100 | 50000 | WL 800 N FS2 UL1066
| FD 100 | 65000 | WL 800 S,H FS2 UL1066
| FD 100 | 85000 | WL 800 L FS2 UL1066
| FD 100 | 20000 | WL 800 F FS2 UL1066
| FD 100 | 50000 | WL 1600 N FS2 UL1066
| FD 100 | 65000 | WL 1600 S,H FS2 UL1066
| FD 100 | 85000 | WL 1600 L FS2 UL1066
| FD 100 | 20000 | WL 1600 F FS2 UL1066
| FD 100 | 65000 | WL 2000 S,H FS2 UL1066
| FD 100 | 85000 | WL 2000 L FS2 UL1066
| FD 100 | 20000 | WL 2000 F FS2 UL1066
| FD 100 | 65000 | WL 3200 S,H FS2 UL1066
| FD 100 | 85000 | WL 3200 L FS2 UL1066
| FD 100 | 100000 | WL 3200 M FS3 UL1066
| FD 100 | 40000 | WL 3200 F FS3 UL1066
| FD 100 | 85000 | WL 4000 H FS3 UL1066
| FD 100 | 100000 | WL 4000 L,M FS3 UL1066
| FD 100 | 40000 | WL 4000 F FS3 UL1066
| FD 100 | 85000 | WL 5000 H FS3 UL1066
| FD 100 | 100000 | WL 5000 L,M FS3 UL1066
| FD 100 | 40000 | WL 5000 F FS3 UL1066
| FD 150 | 1950 | JD 300
| FD 150 | 3200 | JD 400
| FD 150 | 3100 | SJD 300 s
| FD 150 | 4200 | SJD 400 s
| FD 150 | 3200 | LD 400
| FD 150 | 4800 | LD 500
| FD 150 | 4800 | LD 600
| FD 150 | 3100 | SLD 300 s
| FD 150 | 4100 | SLD 400 s
| FD 150 | 5200 | SLD 500 s
| FD 150 | 6200 | SLD 600 s
| FD 150 | 5000 | MD 500
| FD 150 | 6500 | MD 600
| FD 150 | 6500 | MD 800
| FD 150 | 4800 | MG 600
| FD 150 | 5200 | MG 800
| FD 150 | 7200 | SMD 600 s
| FD 150 | 9600 | SMD 800 s
| FD 150 | 4800 | MG 600 s
| FD 150 | 4800 | MG 800 s
| FD 150 | 8000 | ND 1000
| FD 150 | 8000 | ND 1200
| FD 150 | 6400 | NG 800
| FD 150 | 8000 | NG 1000
| FD 150 | 9600 | NG 1200
| FD 150 | 9400 | SND 800 s
| FD 150 | 10000 | SND 1000 s
| FD 150 | 10000 | SND 1200 s
| FD 150 | 7040 | NG 800 s
| FD 150 | 8800 | NG 1000 s
| FD 150 | 9600 | NG 1200 s
| FD 150 | 8000 | PD 1200
| FD 150 | 8000 | PD 1600
| FD 150 | 9600 | PG 1200
| FD 150 | 9600 | PG 1600
| FD 150 | 10000 | SPD 1400 s
| FD 150 | 10000 | SPD 1600 s
| FD 150 | 9600 | PG 1200 s
| FD 150 | 7680 | PG 1600 s
| FD 150 | 52000 | WL 800 FS1 UL489
| FD 150 | 52000 | WL 1200 FS1 UL489
| FD 150 | 52000 | WL 800 FS2 UL489
| FD 150 | 52000 | WL 1200 FS2 UL489
| FD 150 | 52000 | WL 1600 FS2 UL489
| FD 150 | 52000 | WL 2000 FS2 UL489
| FD 150 | 52000 | WL 2500 FS2 UL489
| FD 150 | 52000 | WL 3000 FS2 UL489
| FD 150 | 68000 | WL 4000 FS3 UL489
| FD 150 | 68000 | WL 5000 FS3 UL489
| FD 150 | 50000 | WL 800 N FS2 UL1066
| FD 150 | 65000 | WL 800 S,H FS2 UL1066
| FD 150 | 85000 | WL 800 L FS2 UL1066
| FD 150 | 20000 | WL 800 F FS2 UL1066
| FD 150 | 50000 | WL 1600 N FS2 UL1066
| FD 150 | 65000 | WL 1600 S,H FS2 UL1066
| FD 150 | 85000 | WL 1600 L FS2 UL1066
| FD 150 | 20000 | WL 1600 F FS2 UL1066
| FD 150 | 65000 | WL 2000 S,H FS2 UL1066
| FD 150 | 85000 | WL 2000 L FS2 UL1066
| FD 150 | 20000 | WL 2000 F FS2 UL1066
| FD 150 | 65000 | WL 3200 S,H FS2 UL1066
| FD 150 | 85000 | WL 3200 L FS2 UL1066
| FD 150 | 100000 | WL 3200 M FS3 UL1066
| FD 150 | 40000 | WL 3200 F FS3 UL1066
| FD 150 | 85000 | WL 4000 H FS3 UL1066
| FD 150 | 100000 | WL 4000 L,M FS3 UL1066
| FD 150 | 40000 | WL 4000 F FS3 UL1066
| FD 150 | 85000 | WL 5000 H FS3 UL1066
| FD 150 | 100000 | WL 5000 L,M FS3 UL1066
| FD 150 | 40000 | WL 5000 F FS3 UL1066
| FD 200 | 3200 | JD 400
| FD 200 | 4200 | SJD 400 s
| FD 200 | 3200 | LD 400
| FD 200 | 4800 | LD 500
| FD 200 | 4800 | LD 600
| FD 200 | 4100 | SLD 400 s
| FD 200 | 5200 | SLD 500 s
| FD 200 | 6200 | SLD 600 s
| FD 200 | 5000 | MD 500
| FD 200 | 6500 | MD 600
| FD 200 | 6500 | MD 800
| FD 200 | 4800 | MG 600
| FD 200 | 5200 | MG 800
| FD 200 | 7200 | SMD 600 s
| FD 200 | 9600 | SMD 800 s
| FD 200 | 4800 | MG 600 s
| FD 200 | 4800 | MG 800 s
| FD 200 | 8000 | ND 1000
| FD 200 | 8000 | ND 1200
| FD 200 | 6400 | NG 800
| FD 200 | 8000 | NG 1000
| FD 200 | 9600 | NG 1200
| FD 200 | 9400 | SND 800 s
| FD 200 | 10000 | SND 1000 s
| FD 200 | 10000 | SND 1200 s
| FD 200 | 7040 | NG 800 s
| FD 200 | 8800 | NG 1000 s
| FD 200 | 9600 | NG 1200 s
| FD 200 | 8000 | PD 1200
| FD 200 | 8000 | PD 1600
| FD 200 | 9600 | PG 1200
| FD 200 | 9600 | PG 1600
| FD 200 | 10000 | SPD 1400 s
| FD 200 | 10000 | SPD 1600 s
| FD 200 | 9600 | PG 1200 s
| FD 200 | 7680 | PG 1600 s
| FD 200 | 52000 | WL 800 FS1 UL489
| FD 200 | 52000 | WL 1200 FS1 UL489
| FD 200 | 52000 | WL 800 FS2 UL489
| FD 200 | 52000 | WL 1200 FS2 UL489
| FD 200 | 52000 | WL 1600 FS2 UL489
| FD 200 | 52000 | WL 2000 FS2 UL489
| FD 200 | 52000 | WL 2500 FS2 UL489
| FD 200 | 52000 | WL 3000 FS2 UL489
| FD 200 | 68000 | WL 4000 FS3 UL489
| FD 200 | 68000 | WL 5000 FS3 UL489
| FD 200 | 50000 | WL 800 N FS2 UL1066
| FD 200 | 65000 | WL 800 S,H FS2 UL1066
| FD 200 | 85000 | WL 800 L FS2 UL1066
| FD 200 | 20000 | WL 800 F FS2 UL1066
| FD 200 | 50000 | WL 1600 N FS2 UL1066
| FD 200 | 65000 | WL 1600 S,H FS2 UL1066
| FD 200 | 85000 | WL 1600 L FS2 UL1066
| FD 200 | 20000 | WL 1600 F FS2 UL1066
| FD 200 | 65000 | WL 2000 S,H FS2 UL1066
| FD 200 | 85000 | WL 2000 L FS2 UL1066
| FD 200 | 20000 | WL 2000 F FS2 UL1066
| FD 200 | 65000 | WL 3200 S,H FS2 UL1066
| FD 200 | 85000 | WL 3200 L FS2 UL1066
| FD 200 | 100000 | WL 3200 M FS3 UL1066
| FD 200 | 40000 | WL 3200 F FS3 UL1066
| FD 200 | 85000 | WL 4000 H FS3 UL1066
| FD 200 | 100000 | WL 4000 L,M FS3 UL1066
| FD 200 | 40000 | WL 4000 F FS3 UL1066
| FD 200 | 85000 | WL 5000 H FS3 UL1066
| FD 200 | 100000 | WL 5000 L,M FS3 UL1066
| FD 200 | 40000 | WL 5000 F FS3 UL1066
| FD 250 | 4800 | LD 500
| FD 250 | 4800 | LD 600
| FD 250 | 5200 | SLD 500 s
| FD 250 | 6200 | SLD 600 s
| FD 250 | 5000 | MD 500
| FD 250 | 6500 | MD 600
| FD 250 | 6500 | MD 800
| FD 250 | 4800 | MG 600
| FD 250 | 5200 | MG 800
| FD 250 | 7200 | SMD 600 s
| FD 250 | 9600 | SMD 800 s
| FD 250 | 4800 | MG 600 s
| FD 250 | 4800 | MG 800 s
| FD 250 | 8000 | ND 1000
| FD 250 | 8000 | ND 1200
| FD 250 | 6400 | NG 800
| FD 250 | 8000 | NG 1000
| FD 250 | 9600 | NG 1200
| FD 250 | 9400 | SND 800 s
| FD 250 | 10000 | SND 1000 s
| FD 250 | 10000 | SND 1200 s
| FD 250 | 7040 | NG 800 s
| FD 250 | 8800 | NG 1000 s
| FD 250 | 9600 | NG 1200 s
| FD 250 | 8000 | PD 1200
| FD 250 | 8000 | PD 1600
| FD 250 | 9600 | PG 1200
| FD 250 | 9600 | PG 1600
| FD 250 | 10000 | SPD 1400 s
| FD 250 | 10000 | SPD 1600 s
| FD 250 | 9600 | PG 1200 s
| FD 250 | 7680 | PG 1600 s
| FD 250 | 52000 | WL 800 FS1 UL489
| FD 250 | 52000 | WL 1200 FS1 UL489
| FD 250 | 52000 | WL 800 FS2 UL489
| FD 250 | 52000 | WL 1200 FS2 UL489
| FD 250 | 52000 | WL 1600 FS2 UL489
| FD 250 | 52000 | WL 2000 FS2 UL489
| FD 250 | 52000 | WL 2500 FS2 UL489
| FD 250 | 52000 | WL 3000 FS2 UL489
| FD 250 | 68000 | WL 4000 FS3 UL489
| FD 250 | 68000 | WL 5000 FS3 UL489
| FD 250 | 50000 | WL 800 N FS2 UL1066
| FD 250 | 65000 | WL 800 S,H FS2 UL1066
| FD 250 | 85000 | WL 800 L FS2 UL1066
| FD 250 | 20000 | WL 800 F FS2 UL1066
| FD 250 | 50000 | WL 1600 N FS2 UL1066
| FD 250 | 65000 | WL 1600 S,H FS2 UL1066
| FD 250 | 85000 | WL 1600 L FS2 UL1066
| FD 250 | 20000 | WL 1600 F FS2 UL1066
| FD 250 | 65000 | WL 2000 S,H FS2 UL1066
| FD 250 | 85000 | WL 2000 L FS2 UL1066
| FD 250 | 20000 | WL 2000 F FS2 UL1066
| FD 250 | 65000 | WL 3200 S,H FS2 UL1066
| FD 250 | 85000 | WL 3200 L FS2 UL1066
| FD 250 | 100000 | WL 3200 M FS3 UL1066
| FD 250 | 40000 | WL 3200 F FS3 UL1066
| FD 250 | 85000 | WL 4000 H FS3 UL1066
| FD 250 | 100000 | WL 4000 L,M FS3 UL1066
| FD 250 | 40000 | WL 4000 F FS3 UL1066
| FD 250 | 85000 | WL 5000 H FS3 UL1066
| FD 250 | 100000 | WL 5000 L,M FS3 UL1066
| FD 250 | 40000 | WL 5000 F FS3 UL1066
| JD 300 | 4800 | LD 600
| JD 300 | 6200 | SLD 600 s
| JD 300 | 6500 | MD 600
| JD 300 | 6500 | MD 800
| JD 300 | 4800 | MG 600
| JD 300 | 5200 | MG 800
| JD 300 | 7200 | SMD 600 s
| JD 300 | 9600 | SMD 800 s
| JD 300 | 4800 | MG 800 s
| JD 300 | 8000 | ND 1000
| JD 300 | 8000 | ND 1200
| JD 300 | 6400 | NG 800
| JD 300 | 8000 | NG 1000
| JD 300 | 9600 | NG 1200
| JD 300 | 9400 | SND 800 s
| JD 300 | 10000 | SND 1000 s
| JD 300 | 10000 | SND 1200 s
| JD 300 | 7040 | NG 800 s
| JD 300 | 8800 | NG 1000 s
| JD 300 | 9600 | NG 1200 s
| JD 300 | 8000 | PD 1200
| JD 300 | 8000 | PD 1600
| JD 300 | 9600 | PG 1200
| JD 300 | 9600 | PG 1600
| JD 300 | 10000 | SPD 1400 s
| JD 300 | 10000 | SPD 1600 s
| JD 300 | 9600 | PG 1200 s
| JD 300 | 7680 | PG 1600 s
| JD 300 | 52000 | WL 800 FS1 UL489
| JD 300 | 52000 | WL 1200 FS1 UL489
| JD 300 | 52000 | WL 800 FS2 UL489
| JD 300 | 52000 | WL 1200 FS2 UL489
| JD 300 | 52000 | WL 1600 FS2 UL489
| JD 300 | 52000 | WL 2000 FS2 UL489
| JD 300 | 52000 | WL 2500 FS2 UL489
| JD 300 | 52000 | WL 3000 FS2 UL489
| JD 300 | 68000 | WL 4000 FS3 UL489
| JD 300 | 68000 | WL 5000 FS3 UL489
| JD 300 | 50000 | WL 800 N FS2 UL1066
| JD 300 | 65000 | WL 800 S,H FS2 UL1066
| JD 300 | 85000 | WL 800 L FS2 UL1066
| JD 300 | 20000 | WL 800 F FS2 UL1066
| JD 300 | 50000 | WL 1600 N FS2 UL1066
| JD 300 | 65000 | WL 1600 S,H FS2 UL1066
| JD 300 | 85000 | WL 1600 L FS2 UL1066
| JD 300 | 20000 | WL 1600 F FS2 UL1066
| JD 300 | 65000 | WL 2000 S,H FS2 UL1066
| JD 300 | 85000 | WL 2000 L FS2 UL1066
| JD 300 | 20000 | WL 2000 F FS2 UL1066
| JD 300 | 65000 | WL 3200 S,H FS2 UL1066
| JD 300 | 85000 | WL 3200 L FS2 UL1066
| JD 300 | 100000 | WL 3200 M FS3 UL1066
| JD 300 | 40000 | WL 3200 F FS3 UL1066
| JD 300 | 85000 | WL 4000 H FS3 UL1066
| JD 300 | 100000 | WL 4000 L,M FS3 UL1066
| JD 300 | 40000 | WL 4000 F FS3 UL1066
| JD 300 | 85000 | WL 5000 H FS3 UL1066
| JD 300 | 100000 | WL 5000 L,M FS3 UL1066
| JD 300 | 40000 | WL 5000 F FS3 UL1066
| JD 400 | 6500 | MD 800
| JD 400 | 5200 | MG 800
| JD 400 | 9600 | SMD 800 s
| JD 400 | 4800 | MG 800 s
| JD 400 | 8000 | ND 1000
| JD 400 | 8000 | ND 1200
| JD 400 | 6400 | NG 800
| JD 400 | 8000 | NG 1000
| JD 400 | 9600 | NG 1200
| JD 400 | 9400 | SND 800 s
| JD 400 | 10000 | SND 1000 s
| JD 400 | 10000 | SND 1200 s
| JD 400 | 7040 | NG 800 s
| JD 400 | 8800 | NG 1000 s
| JD 400 | 9600 | NG 1200 s
| JD 400 | 8000 | PD 1200
| JD 400 | 8000 | PD 1600
| JD 400 | 9600 | PG 1200
| JD 400 | 9600 | PG 1600
| JD 400 | 10000 | SPD 1400 s
| JD 400 | 10000 | SPD 1600 s
| JD 400 | 9600 | PG 1200 s
| JD 400 | 7680 | PG 1600 s
| JD 400 | 52000 | WL 800 FS1 UL489
| JD 400 | 52000 | WL 1200 FS1 UL489
| JD 400 | 52000 | WL 800 FS2 UL489
| JD 400 | 52000 | WL 1200 FS2 UL489
| JD 400 | 52000 | WL 1600 FS2 UL489
| JD 400 | 52000 | WL 2000 FS2 UL489
| JD 400 | 52000 | WL 2500 FS2 UL489
| JD 400 | 52000 | WL 3000 FS2 UL489
| JD 400 | 68000 | WL 4000 FS3 UL489
| JD 400 | 68000 | WL 5000 FS3 UL489
| JD 400 | 50000 | WL 800 N FS2 UL1066
| JD 400 | 65000 | WL 800 S,H FS2 UL1066
| JD 400 | 85000 | WL 800 L FS2 UL1066
| JD 400 | 20000 | WL 800 F FS2 UL1066
| JD 400 | 50000 | WL 1600 N FS2 UL1066
| JD 400 | 65000 | WL 1600 S,H FS2 UL1066
| JD 400 | 85000 | WL 1600 L FS2 UL1066
| JD 400 | 20000 | WL 1600 F FS2 UL1066
| JD 400 | 65000 | WL 2000 S,H FS2 UL1066
| JD 400 | 85000 | WL 2000 L FS2 UL1066
| JD 400 | 20000 | WL 2000 F FS2 UL1066
| JD 400 | 65000 | WL 3200 S,H FS2 UL1066
| JD 400 | 85000 | WL 3200 L FS2 UL1066
| JD 400 | 100000 | WL 3200 M FS3 UL1066
| JD 400 | 40000 | WL 3200 F FS3 UL1066
| JD 400 | 85000 | WL 4000 H FS3 UL1066
| JD 400 | 100000 | WL 4000 L,M FS3 UL1066
| JD 400 | 40000 | WL 4000 F FS3 UL1066
| JD 400 | 85000 | WL 5000 H FS3 UL1066
| JD 400 | 100000 | WL 5000 L,M FS3 UL1066
| JD 400 | 40000 | WL 5000 F FS3 UL1066
| SJD 200 s | 3200 | JD 400
| SJD 200 s | 4200 | SJD 400 s
| SJD 200 s | 3200 | LD 400
| SJD 200 s | 4800 | LD 500
| SJD 200 s | 4800 | LD 600
| SJD 200 s | 4100 | SLD 400 s
| SJD 200 s | 5200 | SLD 500 s
| SJD 200 s | 6200 | SLD 600 s
| SJD 200 s | 5000 | MD 500
| SJD 200 s | 6500 | MD 600
| SJD 200 s | 6500 | MD 800
| SJD 200 s | 4800 | MG 600
| SJD 200 s | 5200 | MG 800
| SJD 200 s | 7200 | SMD 600 s
| SJD 200 s | 9600 | SMD 800 s
| SJD 200 s | 4800 | MG 600 s
| SJD 200 s | 4800 | MG 800 s
| SJD 200 s | 8000 | ND 1000
| SJD 200 s | 8000 | ND 1200
| SJD 200 s | 6400 | NG 800
| SJD 200 s | 8000 | NG 1000
| SJD 200 s | 9600 | NG 1200
| SJD 200 s | 9400 | SND 800 s
| SJD 200 s | 10000 | SND 1000 s
| SJD 200 s | 10000 | SND 1200 s
| SJD 200 s | 7040 | NG 800 s
| SJD 200 s | 8800 | NG 1000 s
| SJD 200 s | 9600 | NG 1200 s
| SJD 200 s | 8000 | PD 1200
| SJD 200 s | 8000 | PD 1600
| SJD 200 s | 9600 | PG 1200
| SJD 200 s | 9600 | PG 1600
| SJD 200 s | 10000 | SPD 1400 s
| SJD 200 s | 10000 | SPD 1600 s
| SJD 200 s | 9600 | PG 1200 s
| SJD 200 s | 7680 | PG 1600 s
| SJD 200 s | 52000 | WL 800 FS1 UL489
| SJD 200 s | 52000 | WL 1200 FS1 UL489
| SJD 200 s | 52000 | WL 800 FS2 UL489
| SJD 200 s | 52000 | WL 1200 FS2 UL489
| SJD 200 s | 52000 | WL 1600 FS2 UL489
| SJD 200 s | 52000 | WL 2000 FS2 UL489
| SJD 200 s | 52000 | WL 2500 FS2 UL489
| SJD 200 s | 52000 | WL 3000 FS2 UL489
| SJD 200 s | 68000 | WL 4000 FS3 UL489
| SJD 200 s | 68000 | WL 5000 FS3 UL489
| SJD 200 s | 50000 | WL 800 N FS2 UL1066
| SJD 200 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 800 L FS2 UL1066
| SJD 200 s | 20000 | WL 800 F FS2 UL1066
| SJD 200 s | 50000 | WL 1600 N FS2 UL1066
| SJD 200 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 1600 L FS2 UL1066
| SJD 200 s | 20000 | WL 1600 F FS2 UL1066
| SJD 200 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 2000 L FS2 UL1066
| SJD 200 s | 20000 | WL 2000 F FS2 UL1066
| SJD 200 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 200 s | 85000 | WL 3200 L FS2 UL1066
| SJD 200 s | 100000 | WL 3200 M FS3 UL1066
| SJD 200 s | 40000 | WL 3200 F FS3 UL1066
| SJD 200 s | 85000 | WL 4000 H FS3 UL1066
| SJD 200 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 200 s | 40000 | WL 4000 F FS3 UL1066
| SJD 200 s | 85000 | WL 5000 H FS3 UL1066
| SJD 200 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 200 s | 40000 | WL 5000 F FS3 UL1066
| SJD 300 s | 4800 | LD 600
| SJD 300 s | 6200 | SLD 600 s
| SJD 300 s | 6500 | MD 600
| SJD 300 s | 6500 | MD 800
| SJD 300 s | 4800 | MG 600
| SJD 300 s | 5200 | MG 800
| SJD 300 s | 7200 | SMD 600 s
| SJD 300 s | 9600 | SMD 800 s
| SJD 300 s | 4800 | MG 800 s
| SJD 300 s | 8000 | ND 1000
| SJD 300 s | 8000 | ND 1200
| SJD 300 s | 6400 | NG 800
| SJD 300 s | 8000 | NG 1000
| SJD 300 s | 9600 | NG 1200
| SJD 300 s | 9400 | SND 800 s
| SJD 300 s | 10000 | SND 1000 s
| SJD 300 s | 10000 | SND 1200 s
| SJD 300 s | 7040 | NG 800 s
| SJD 300 s | 8800 | NG 1000 s
| SJD 300 s | 9600 | NG 1200 s
| SJD 300 s | 8000 | PD 1200
| SJD 300 s | 8000 | PD 1600
| SJD 300 s | 9600 | PG 1200
| SJD 300 s | 9600 | PG 1600
| SJD 300 s | 10000 | SPD 1400 s
| SJD 300 s | 10000 | SPD 1600 s
| SJD 300 s | 9600 | PG 1200 s
| SJD 300 s | 7680 | PG 1600 s
| SJD 300 s | 52000 | WL 800 FS1 UL489
| SJD 300 s | 52000 | WL 1200 FS1 UL489
| SJD 300 s | 52000 | WL 800 FS2 UL489
| SJD 300 s | 52000 | WL 1200 FS2 UL489
| SJD 300 s | 52000 | WL 1600 FS2 UL489
| SJD 300 s | 52000 | WL 2000 FS2 UL489
| SJD 300 s | 52000 | WL 2500 FS2 UL489
| SJD 300 s | 52000 | WL 3000 FS2 UL489
| SJD 300 s | 68000 | WL 4000 FS3 UL489
| SJD 300 s | 68000 | WL 5000 FS3 UL489
| SJD 300 s | 50000 | WL 800 N FS2 UL1066
| SJD 300 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 800 L FS2 UL1066
| SJD 300 s | 20000 | WL 800 F FS2 UL1066
| SJD 300 s | 50000 | WL 1600 N FS2 UL1066
| SJD 300 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 1600 L FS2 UL1066
| SJD 300 s | 20000 | WL 1600 F FS2 UL1066
| SJD 300 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 2000 L FS2 UL1066
| SJD 300 s | 20000 | WL 2000 F FS2 UL1066
| SJD 300 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 300 s | 85000 | WL 3200 L FS2 UL1066
| SJD 300 s | 100000 | WL 3200 M FS3 UL1066
| SJD 300 s | 40000 | WL 3200 F FS3 UL1066
| SJD 300 s | 85000 | WL 4000 H FS3 UL1066
| SJD 300 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 300 s | 40000 | WL 4000 F FS3 UL1066
| SJD 300 s | 85000 | WL 5000 H FS3 UL1066
| SJD 300 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 300 s | 40000 | WL 5000 F FS3 UL1066
| SJD 400 s | 6500 | MD 800
| SJD 400 s | 5200 | MG 800
| SJD 400 s | 9600 | SMD 800 s
| SJD 400 s | 4800 | MG 800 s
| SJD 400 s | 8000 | ND 1000
| SJD 400 s | 8000 | ND 1200
| SJD 400 s | 6400 | NG 800
| SJD 400 s | 8000 | NG 1000
| SJD 400 s | 9600 | NG 1200
| SJD 400 s | 9400 | SND 800 s
| SJD 400 s | 10000 | SND 1000 s
| SJD 400 s | 10000 | SND 1200 s
| SJD 400 s | 7040 | NG 800 s
| SJD 400 s | 8800 | NG 1000 s
| SJD 400 s | 9600 | NG 1200 s
| SJD 400 s | 8000 | PD 1200
| SJD 400 s | 8000 | PD 1600
| SJD 400 s | 9600 | PG 1200
| SJD 400 s | 9600 | PG 1600
| SJD 400 s | 10000 | SPD 1400 s
| SJD 400 s | 10000 | SPD 1600 s
| SJD 400 s | 9600 | PG 1200 s
| SJD 400 s | 7680 | PG 1600 s
| SJD 400 s | 52000 | WL 800 FS1 UL489
| SJD 400 s | 52000 | WL 1200 FS1 UL489
| SJD 400 s | 52000 | WL 800 FS2 UL489
| SJD 400 s | 52000 | WL 1200 FS2 UL489
| SJD 400 s | 52000 | WL 1600 FS2 UL489
| SJD 400 s | 52000 | WL 2000 FS2 UL489
| SJD 400 s | 52000 | WL 2500 FS2 UL489
| SJD 400 s | 52000 | WL 3000 FS2 UL489
| SJD 400 s | 68000 | WL 4000 FS3 UL489
| SJD 400 s | 68000 | WL 5000 FS3 UL489
| SJD 400 s | 50000 | WL 800 N FS2 UL1066
| SJD 400 s | 65000 | WL 800 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 800 L FS2 UL1066
| SJD 400 s | 20000 | WL 800 F FS2 UL1066
| SJD 400 s | 50000 | WL 1600 N FS2 UL1066
| SJD 400 s | 65000 | WL 1600 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 1600 L FS2 UL1066
| SJD 400 s | 20000 | WL 1600 F FS2 UL1066
| SJD 400 s | 65000 | WL 2000 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 2000 L FS2 UL1066
| SJD 400 s | 20000 | WL 2000 F FS2 UL1066
| SJD 400 s | 65000 | WL 3200 S,H FS2 UL1066
| SJD 400 s | 85000 | WL 3200 L FS2 UL1066
| SJD 400 s | 100000 | WL 3200 M FS3 UL1066
| SJD 400 s | 40000 | WL 3200 F FS3 UL1066
| SJD 400 s | 85000 | WL 4000 H FS3 UL1066
| SJD 400 s | 100000 | WL 4000 L,M FS3 UL1066
| SJD 400 s | 40000 | WL 4000 F FS3 UL1066
| SJD 400 s | 85000 | WL 5000 H FS3 UL1066
| SJD 400 s | 100000 | WL 5000 L,M FS3 UL1066
| SJD 400 s | 40000 | WL 5000 F FS3 UL1066
| LD 250 | 4800 | LD 600
| LD 250 | 5200 | SLD 500 s
| LD 250 | 6200 | SLD 600 s
| LD 250 | 5000 | MD 500
| LD 250 | 6500 | MD 600
| LD 250 | 6500 | MD 800
| LD 250 | 4800 | MG 600
| LD 250 | 5200 | MG 800
| LD 250 | 7200 | SMD 600 s
| LD 250 | 9600 | SMD 800 s
| LD 250 | 4800 | MG 600 s
| LD 250 | 4800 | MG 800 s
| LD 250 | 8000 | ND 1000
| LD 250 | 8000 | ND 1200
| LD 250 | 6400 | NG 800
| LD 250 | 8000 | NG 1000
| LD 250 | 9600 | NG 1200
| LD 250 | 9400 | SND 800 s
| LD 250 | 10000 | SND 1000 s
| LD 250 | 10000 | SND 1200 s
| LD 250 | 7040 | NG 800 s
| LD 250 | 8800 | NG 1000 s
| LD 250 | 9600 | NG 1200 s
| LD 250 | 8000 | PD 1200
| LD 250 | 8000 | PD 1600
| LD 250 | 9600 | PG 1200
| LD 250 | 9600 | PG 1600
| LD 250 | 10000 | SPD 1400 s
| LD 250 | 10000 | SPD 1600 s
| LD 250 | 9600 | PG 1200 s
| LD 250 | 7680 | PG 1600 s
| LD 250 | 52000 | WL 800 FS1 UL489
| LD 250 | 52000 | WL 1200 FS1 UL489
| LD 250 | 52000 | WL 800 FS2 UL489
| LD 250 | 52000 | WL 1200 FS2 UL489
| LD 250 | 52000 | WL 1600 FS2 UL489
| LD 250 | 52000 | WL 2000 FS2 UL489
| LD 250 | 52000 | WL 2500 FS2 UL489
| LD 250 | 52000 | WL 3000 FS2 UL489
| LD 250 | 68000 | WL 4000 FS3 UL489
| LD 250 | 68000 | WL 5000 FS3 UL489
| LD 250 | 50000 | WL 800 N FS2 UL1066
| LD 250 | 65000 | WL 800 S,H FS2 UL1066
| LD 250 | 85000 | WL 800 L FS2 UL1066
| LD 250 | 20000 | WL 800 F FS2 UL1066
| LD 250 | 50000 | WL 1600 N FS2 UL1066
| LD 250 | 65000 | WL 1600 S,H FS2 UL1066
| LD 250 | 85000 | WL 1600 L FS2 UL1066
| LD 250 | 20000 | WL 1600 F FS2 UL1066
| LD 250 | 65000 | WL 2000 S,H FS2 UL1066
| LD 250 | 85000 | WL 2000 L FS2 UL1066
| LD 250 | 20000 | WL 2000 F FS2 UL1066
| LD 250 | 65000 | WL 3200 S,H FS2 UL1066
| LD 250 | 85000 | WL 3200 L FS2 UL1066
| LD 250 | 100000 | WL 3200 M FS3 UL1066
| LD 250 | 40000 | WL 3200 F FS3 UL1066
| LD 250 | 85000 | WL 4000 H FS3 UL1066
| LD 250 | 100000 | WL 4000 L,M FS3 UL1066
| LD 250 | 40000 | WL 4000 F FS3 UL1066
| LD 250 | 85000 | WL 5000 H FS3 UL1066
| LD 250 | 100000 | WL 5000 L,M FS3 UL1066
| LD 250 | 40000 | WL 5000 F FS3 UL1066
| LD 400 | 6500 | MD 800
| LD 400 | 5200 | MG 800
| LD 400 | 9600 | SMD 800 s
| LD 400 | 8000 | ND 1000
| LD 400 | 8000 | ND 1200
| LD 400 | 6400 | NG 800
| LD 400 | 8000 | NG 1000
| LD 400 | 9600 | NG 1200
| LD 400 | 9400 | SND 800 s
| LD 400 | 10000 | SND 1000 s
| LD 400 | 10000 | SND 1200 s
| LD 400 | 7040 | NG 800 s
| LD 400 | 8800 | NG 1000 s
| LD 400 | 9600 | NG 1200 s
| LD 400 | 8000 | PD 1200
| LD 400 | 8000 | PD 1600
| LD 400 | 9600 | PG 1200
| LD 400 | 9600 | PG 1600
| LD 400 | 10000 | SPD 1400 s
| LD 400 | 10000 | SPD 1600 s
| LD 400 | 9600 | PG 1200 s
| LD 400 | 7680 | PG 1600 s
| LD 400 | 52000 | WL 800 FS1 UL489
| LD 400 | 52000 | WL 1200 FS1 UL489
| LD 400 | 52000 | WL 800 FS2 UL489
| LD 400 | 52000 | WL 1200 FS2 UL489
| LD 400 | 52000 | WL 1600 FS2 UL489
| LD 400 | 52000 | WL 2000 FS2 UL489
| LD 400 | 52000 | WL 2500 FS2 UL489
| LD 400 | 52000 | WL 3000 FS2 UL489
| LD 400 | 68000 | WL 4000 FS3 UL489
| LD 400 | 68000 | WL 5000 FS3 UL489
| LD 400 | 50000 | WL 800 N FS2 UL1066
| LD 400 | 65000 | WL 800 S,H FS2 UL1066
| LD 400 | 85000 | WL 800 L FS2 UL1066
| LD 400 | 20000 | WL 800 F FS2 UL1066
| LD 400 | 50000 | WL 1600 N FS2 UL1066
| LD 400 | 65000 | WL 1600 S,H FS2 UL1066
| LD 400 | 85000 | WL 1600 L FS2 UL1066
| LD 400 | 20000 | WL 1600 F FS2 UL1066
| LD 400 | 65000 | WL 2000 S,H FS2 UL1066
| LD 400 | 85000 | WL 2000 L FS2 UL1066
| LD 400 | 20000 | WL 2000 F FS2 UL1066
| LD 400 | 65000 | WL 3200 S,H FS2 UL1066
| LD 400 | 85000 | WL 3200 L FS2 UL1066
| LD 400 | 100000 | WL 3200 M FS3 UL1066
| LD 400 | 40000 | WL 3200 F FS3 UL1066
| LD 400 | 85000 | WL 4000 H FS3 UL1066
| LD 400 | 100000 | WL 4000 L,M FS3 UL1066
| LD 400 | 40000 | WL 4000 F FS3 UL1066
| LD 400 | 85000 | WL 5000 H FS3 UL1066
| LD 400 | 100000 | WL 5000 L,M FS3 UL1066
| LD 400 | 40000 | WL 5000 F FS3 UL1066
| LD 500 | 8000 | ND 1000
| LD 500 | 8000 | ND 1200
| LD 500 | 8000 | NG 1000
| LD 500 | 9600 | NG 1200
| LD 500 | 10000 | SND 1200 s
| LD 500 | 8800 | NG 1000 s
| LD 500 | 9600 | NG 1200 s
| LD 500 | 8000 | PD 1200
| LD 500 | 8000 | PD 1600
| LD 500 | 9600 | PG 1200
| LD 500 | 9600 | PG 1600
| LD 500 | 10000 | SPD 1400 s
| LD 500 | 10000 | SPD 1600 s
| LD 500 | 9600 | PG 1200 s
| LD 500 | 7680 | PG 1600 s
| LD 500 | 52000 | WL 1200 FS1 UL489
| LD 500 | 52000 | WL 1200 FS2 UL489
| LD 500 | 52000 | WL 1600 FS2 UL489
| LD 500 | 52000 | WL 2000 FS2 UL489
| LD 500 | 52000 | WL 2500 FS2 UL489
| LD 500 | 52000 | WL 3000 FS2 UL489
| LD 500 | 68000 | WL 4000 FS3 UL489
| LD 500 | 68000 | WL 5000 FS3 UL489
| LD 500 | 50000 | WL 1600 N FS2 UL1066
| LD 500 | 65000 | WL 1600 S,H FS2 UL1066
| LD 500 | 85000 | WL 1600 L FS2 UL1066
| LD 500 | 20000 | WL 1600 F FS2 UL1066
| LD 500 | 65000 | WL 2000 S,H FS2 UL1066
| LD 500 | 85000 | WL 2000 L FS2 UL1066
| LD 500 | 20000 | WL 2000 F FS2 UL1066
| LD 500 | 65000 | WL 3200 S,H FS2 UL1066
| LD 500 | 85000 | WL 3200 L FS2 UL1066
| LD 500 | 100000 | WL 3200 M FS3 UL1066
| LD 500 | 40000 | WL 3200 F FS3 UL1066
| LD 500 | 85000 | WL 4000 H FS3 UL1066
| LD 500 | 100000 | WL 4000 L,M FS3 UL1066
| LD 500 | 40000 | WL 4000 F FS3 UL1066
| LD 500 | 85000 | WL 5000 H FS3 UL1066
| LD 500 | 100000 | WL 5000 L,M FS3 UL1066
| LD 500 | 40000 | WL 5000 F FS3 UL1066
| LD 600 | 9600 | NG 1200
| LD 600 | 10000 | SND 1200 s
| LD 600 | 9600 | NG 1200 s
| LD 600 | 8000 | PD 1200
| LD 600 | 8000 | PD 1600
| LD 600 | 9600 | PG 1200
| LD 600 | 9600 | PG 1600
| LD 600 | 10000 | SPD 1400 s
| LD 600 | 10000 | SPD 1600 s
| LD 600 | 9600 | PG 1200 s
| LD 600 | 7680 | PG 1600 s
| LD 600 | 52000 | WL 1200 FS1 UL489
| LD 600 | 52000 | WL 1200 FS2 UL489
| LD 600 | 52000 | WL 1600 FS2 UL489
| LD 600 | 52000 | WL 2000 FS2 UL489
| LD 600 | 52000 | WL 2500 FS2 UL489
| LD 600 | 52000 | WL 3000 FS2 UL489
| LD 600 | 68000 | WL 4000 FS3 UL489
| LD 600 | 68000 | WL 5000 FS3 UL489
| LD 600 | 50000 | WL 1600 N FS2 UL1066
| LD 600 | 65000 | WL 1600 S,H FS2 UL1066
| LD 600 | 85000 | WL 1600 L FS2 UL1066
| LD 600 | 20000 | WL 1600 F FS2 UL1066
| LD 600 | 65000 | WL 2000 S,H FS2 UL1066
| LD 600 | 85000 | WL 2000 L FS2 UL1066
| LD 600 | 20000 | WL 2000 F FS2 UL1066
| LD 600 | 65000 | WL 3200 S,H FS2 UL1066
| LD 600 | 85000 | WL 3200 L FS2 UL1066
| LD 600 | 100000 | WL 3200 M FS3 UL1066
| LD 600 | 40000 | WL 3200 F FS3 UL1066
| LD 600 | 85000 | WL 4000 H FS3 UL1066
| LD 600 | 100000 | WL 4000 L,M FS3 UL1066
| LD 600 | 40000 | WL 4000 F FS3 UL1066
| LD 600 | 85000 | WL 5000 H FS3 UL1066
| LD 600 | 100000 | WL 5000 L,M FS3 UL1066
| LD 600 | 40000 | WL 5000 F FS3 UL1066
| SLD 300 s | 4800 | LD 600
| SLD 300 s | 5200 | SLD 500 s
| SLD 300 s | 6200 | SLD 600 s
| SLD 300 s | 6500 | MD 600
| SLD 300 s | 6500 | MD 800
| SLD 300 s | 4800 | MG 600
| SLD 300 s | 5200 | MG 800
| SLD 300 s | 7200 | SMD 600 s
| SLD 300 s | 9600 | SMD 800 s
| SLD 300 s | 4800 | MG 800 s
| SLD 300 s | 8000 | ND 1000
| SLD 300 s | 8000 | ND 1200
| SLD 300 s | 6400 | NG 800
| SLD 300 s | 8000 | NG 1000
| SLD 300 s | 9600 | NG 1200
| SLD 300 s | 9400 | SND 800 s
| SLD 300 s | 10000 | SND 1000 s
| SLD 300 s | 10000 | SND 1200 s
| SLD 300 s | 7040 | NG 800 s
| SLD 300 s | 8800 | NG 1000 s
| SLD 300 s | 9600 | NG 1200 s
| SLD 300 s | 8000 | PD 1200
| SLD 300 s | 8000 | PD 1600
| SLD 300 s | 9600 | PG 1200
| SLD 300 s | 9600 | PG 1600
| SLD 300 s | 10000 | SPD 1400 s
| SLD 300 s | 10000 | SPD 1600 s
| SLD 300 s | 9600 | PG 1200 s
| SLD 300 s | 7680 | PG 1600 s
| SLD 300 s | 52000 | WL 800 FS1 UL489
| SLD 300 s | 52000 | WL 1200 FS1 UL489
| SLD 300 s | 52000 | WL 800 FS2 UL489
| SLD 300 s | 52000 | WL 1200 FS2 UL489
| SLD 300 s | 52000 | WL 1600 FS2 UL489
| SLD 300 s | 52000 | WL 2000 FS2 UL489
| SLD 300 s | 52000 | WL 2500 FS2 UL489
| SLD 300 s | 52000 | WL 3000 FS2 UL489
| SLD 300 s | 68000 | WL 4000 FS3 UL489
| SLD 300 s | 68000 | WL 5000 FS3 UL489
| SLD 300 s | 50000 | WL 800 N FS2 UL1066
| SLD 300 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 800 L FS2 UL1066
| SLD 300 s | 20000 | WL 800 F FS2 UL1066
| SLD 300 s | 50000 | WL 1600 N FS2 UL1066
| SLD 300 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 1600 L FS2 UL1066
| SLD 300 s | 20000 | WL 1600 F FS2 UL1066
| SLD 300 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 2000 L FS2 UL1066
| SLD 300 s | 20000 | WL 2000 F FS2 UL1066
| SLD 300 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 300 s | 85000 | WL 3200 L FS2 UL1066
| SLD 300 s | 100000 | WL 3200 M FS3 UL1066
| SLD 300 s | 40000 | WL 3200 F FS3 UL1066
| SLD 300 s | 85000 | WL 4000 H FS3 UL1066
| SLD 300 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 300 s | 40000 | WL 4000 F FS3 UL1066
| SLD 300 s | 85000 | WL 5000 H FS3 UL1066
| SLD 300 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 300 s | 40000 | WL 5000 F FS3 UL1066
| SLD 400 s | 6200 | SLD 600 s
| SLD 400 s | 6500 | MD 800
| SLD 400 s | 5200 | MG 800
| SLD 400 s | 7200 | SMD 600 s
| SLD 400 s | 9600 | SMD 800 s
| SLD 400 s | 4800 | MG 800 s
| SLD 400 s | 8000 | ND 1000
| SLD 400 s | 8000 | ND 1200
| SLD 400 s | 6400 | NG 800
| SLD 400 s | 8000 | NG 1000
| SLD 400 s | 9600 | NG 1200
| SLD 400 s | 9400 | SND 800 s
| SLD 400 s | 10000 | SND 1000 s
| SLD 400 s | 10000 | SND 1200 s
| SLD 400 s | 7040 | NG 800 s
| SLD 400 s | 8800 | NG 1000 s
| SLD 400 s | 9600 | NG 1200 s
| SLD 400 s | 8000 | PD 1200
| SLD 400 s | 8000 | PD 1600
| SLD 400 s | 9600 | PG 1200
| SLD 400 s | 9600 | PG 1600
| SLD 400 s | 10000 | SPD 1400 s
| SLD 400 s | 10000 | SPD 1600 s
| SLD 400 s | 9600 | PG 1200 s
| SLD 400 s | 7680 | PG 1600 s
| SLD 400 s | 52000 | WL 800 FS1 UL489
| SLD 400 s | 52000 | WL 1200 FS1 UL489
| SLD 400 s | 52000 | WL 800 FS2 UL489
| SLD 400 s | 52000 | WL 1200 FS2 UL489
| SLD 400 s | 52000 | WL 1600 FS2 UL489
| SLD 400 s | 52000 | WL 2000 FS2 UL489
| SLD 400 s | 52000 | WL 2500 FS2 UL489
| SLD 400 s | 52000 | WL 3000 FS2 UL489
| SLD 400 s | 68000 | WL 4000 FS3 UL489
| SLD 400 s | 68000 | WL 5000 FS3 UL489
| SLD 400 s | 50000 | WL 800 N FS2 UL1066
| SLD 400 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 800 L FS2 UL1066
| SLD 400 s | 20000 | WL 800 F FS2 UL1066
| SLD 400 s | 50000 | WL 1600 N FS2 UL1066
| SLD 400 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 1600 L FS2 UL1066
| SLD 400 s | 20000 | WL 1600 F FS2 UL1066
| SLD 400 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 2000 L FS2 UL1066
| SLD 400 s | 20000 | WL 2000 F FS2 UL1066
| SLD 400 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 400 s | 85000 | WL 3200 L FS2 UL1066
| SLD 400 s | 100000 | WL 3200 M FS3 UL1066
| SLD 400 s | 40000 | WL 3200 F FS3 UL1066
| SLD 400 s | 85000 | WL 4000 H FS3 UL1066
| SLD 400 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 400 s | 40000 | WL 4000 F FS3 UL1066
| SLD 400 s | 85000 | WL 5000 H FS3 UL1066
| SLD 400 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 400 s | 40000 | WL 5000 F FS3 UL1066
| SLD 500 s | 5200 | MG 800
| SLD 500 s | 9600 | SMD 800 s
| SLD 500 s | 8000 | ND 1000
| SLD 500 s | 8000 | ND 1200
| SLD 500 s | 6400 | NG 800
| SLD 500 s | 8000 | NG 1000
| SLD 500 s | 9600 | NG 1200
| SLD 500 s | 9400 | SND 800 s
| SLD 500 s | 10000 | SND 1000 s
| SLD 500 s | 10000 | SND 1200 s
| SLD 500 s | 7040 | NG 800 s
| SLD 500 s | 8800 | NG 1000 s
| SLD 500 s | 9600 | NG 1200 s
| SLD 500 s | 8000 | PD 1200
| SLD 500 s | 8000 | PD 1600
| SLD 500 s | 9600 | PG 1200
| SLD 500 s | 9600 | PG 1600
| SLD 500 s | 10000 | SPD 1400 s
| SLD 500 s | 10000 | SPD 1600 s
| SLD 500 s | 9600 | PG 1200 s
| SLD 500 s | 7680 | PG 1600 s
| SLD 500 s | 52000 | WL 800 FS1 UL489
| SLD 500 s | 52000 | WL 1200 FS1 UL489
| SLD 500 s | 52000 | WL 800 FS2 UL489
| SLD 500 s | 52000 | WL 1200 FS2 UL489
| SLD 500 s | 52000 | WL 1600 FS2 UL489
| SLD 500 s | 52000 | WL 2000 FS2 UL489
| SLD 500 s | 52000 | WL 2500 FS2 UL489
| SLD 500 s | 52000 | WL 3000 FS2 UL489
| SLD 500 s | 68000 | WL 4000 FS3 UL489
| SLD 500 s | 68000 | WL 5000 FS3 UL489
| SLD 500 s | 50000 | WL 800 N FS2 UL1066
| SLD 500 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 800 L FS2 UL1066
| SLD 500 s | 20000 | WL 800 F FS2 UL1066
| SLD 500 s | 50000 | WL 1600 N FS2 UL1066
| SLD 500 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 1600 L FS2 UL1066
| SLD 500 s | 20000 | WL 1600 F FS2 UL1066
| SLD 500 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 2000 L FS2 UL1066
| SLD 500 s | 20000 | WL 2000 F FS2 UL1066
| SLD 500 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 500 s | 85000 | WL 3200 L FS2 UL1066
| SLD 500 s | 100000 | WL 3200 M FS3 UL1066
| SLD 500 s | 40000 | WL 3200 F FS3 UL1066
| SLD 500 s | 85000 | WL 4000 H FS3 UL1066
| SLD 500 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 500 s | 40000 | WL 4000 F FS3 UL1066
| SLD 500 s | 85000 | WL 5000 H FS3 UL1066
| SLD 500 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 500 s | 40000 | WL 5000 F FS3 UL1066
| SLD 600 s | 9600 | SMD 800 s
| SLD 600 s | 8000 | ND 1200
| SLD 600 s | 8000 | NG 1000
| SLD 600 s | 9600 | NG 1200
| SLD 600 s | 9400 | SND 800 s
| SLD 600 s | 10000 | SND 1000 s
| SLD 600 s | 10000 | SND 1200 s
| SLD 600 s | 7040 | NG 800 s
| SLD 600 s | 8800 | NG 1000 s
| SLD 600 s | 9600 | NG 1200 s
| SLD 600 s | 8000 | PD 1200
| SLD 600 s | 8000 | PD 1600
| SLD 600 s | 9600 | PG 1200
| SLD 600 s | 9600 | PG 1600
| SLD 600 s | 10000 | SPD 1400 s
| SLD 600 s | 10000 | SPD 1600 s
| SLD 600 s | 9600 | PG 1200 s
| SLD 600 s | 7680 | PG 1600 s
| SLD 600 s | 52000 | WL 800 FS1 UL489
| SLD 600 s | 52000 | WL 1200 FS1 UL489
| SLD 600 s | 52000 | WL 800 FS2 UL489
| SLD 600 s | 52000 | WL 1200 FS2 UL489
| SLD 600 s | 52000 | WL 1600 FS2 UL489
| SLD 600 s | 52000 | WL 2000 FS2 UL489
| SLD 600 s | 52000 | WL 2500 FS2 UL489
| SLD 600 s | 52000 | WL 3000 FS2 UL489
| SLD 600 s | 68000 | WL 4000 FS3 UL489
| SLD 600 s | 68000 | WL 5000 FS3 UL489
| SLD 600 s | 50000 | WL 800 N FS2 UL1066
| SLD 600 s | 65000 | WL 800 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 800 L FS2 UL1066
| SLD 600 s | 20000 | WL 800 F FS2 UL1066
| SLD 600 s | 50000 | WL 1600 N FS2 UL1066
| SLD 600 s | 65000 | WL 1600 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 1600 L FS2 UL1066
| SLD 600 s | 20000 | WL 1600 F FS2 UL1066
| SLD 600 s | 65000 | WL 2000 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 2000 L FS2 UL1066
| SLD 600 s | 20000 | WL 2000 F FS2 UL1066
| SLD 600 s | 65000 | WL 3200 S,H FS2 UL1066
| SLD 600 s | 85000 | WL 3200 L FS2 UL1066
| SLD 600 s | 100000 | WL 3200 M FS3 UL1066
| SLD 600 s | 40000 | WL 3200 F FS3 UL1066
| SLD 600 s | 85000 | WL 4000 H FS3 UL1066
| SLD 600 s | 100000 | WL 4000 L,M FS3 UL1066
| SLD 600 s | 40000 | WL 4000 F FS3 UL1066
| SLD 600 s | 85000 | WL 5000 H FS3 UL1066
| SLD 600 s | 100000 | WL 5000 L,M FS3 UL1066
| SLD 600 s | 40000 | WL 5000 F FS3 UL1066
| MD 500 | 9600 | NG 1200 s
| MD 500 | 10000 | SPD 1400 s
| MD 500 | 10000 | SPD 1600 s
| MD 500 | 9600 | PG 1200 s
| MD 500 | 7680 | PG 1600 s
| MD 500 | 52000 | WL 1600 FS2 UL489
| MD 500 | 52000 | WL 2000 FS2 UL489
| MD 500 | 52000 | WL 2500 FS2 UL489
| MD 500 | 52000 | WL 3000 FS2 UL489
| MD 500 | 68000 | WL 4000 FS3 UL489
| MD 500 | 68000 | WL 5000 FS3 UL489
| MD 500 | 50000 | WL 1600 N FS2 UL1066
| MD 500 | 65000 | WL 1600 S,H FS2 UL1066
| MD 500 | 85000 | WL 1600 L FS2 UL1066
| MD 500 | 20000 | WL 1600 F FS2 UL1066
| MD 500 | 65000 | WL 2000 S,H FS2 UL1066
| MD 500 | 85000 | WL 2000 L FS2 UL1066
| MD 500 | 20000 | WL 2000 F FS2 UL1066
| MD 500 | 65000 | WL 3200 S,H FS2 UL1066
| MD 500 | 85000 | WL 3200 L FS2 UL1066
| MD 500 | 100000 | WL 3200 M FS3 UL1066
| MD 500 | 40000 | WL 3200 F FS3 UL1066
| MD 500 | 85000 | WL 4000 H FS3 UL1066
| MD 500 | 100000 | WL 4000 L,M FS3 UL1066
| MD 500 | 40000 | WL 4000 F FS3 UL1066
| MD 500 | 85000 | WL 5000 H FS3 UL1066
| MD 500 | 100000 | WL 5000 L,M FS3 UL1066
| MD 500 | 40000 | WL 5000 F FS3 UL1066
| MD 600 | 10000 | SPD 1600 s
| MD 600 | 52000 | WL 1600 FS2 UL489
| MD 600 | 52000 | WL 2000 FS2 UL489
| MD 600 | 52000 | WL 2500 FS2 UL489
| MD 600 | 52000 | WL 3000 FS2 UL489
| MD 600 | 68000 | WL 4000 FS3 UL489
| MD 600 | 68000 | WL 5000 FS3 UL489
| MD 600 | 50000 | WL 1600 N FS2 UL1066
| MD 600 | 65000 | WL 1600 S,H FS2 UL1066
| MD 600 | 85000 | WL 1600 L FS2 UL1066
| MD 600 | 20000 | WL 1600 F FS2 UL1066
| MD 600 | 65000 | WL 2000 S,H FS2 UL1066
| MD 600 | 85000 | WL 2000 L FS2 UL1066
| MD 600 | 20000 | WL 2000 F FS2 UL1066
| MD 600 | 65000 | WL 3200 S,H FS2 UL1066
| MD 600 | 85000 | WL 3200 L FS2 UL1066
| MD 600 | 100000 | WL 3200 M FS3 UL1066
| MD 600 | 40000 | WL 3200 F FS3 UL1066
| MD 600 | 85000 | WL 4000 H FS3 UL1066
| MD 600 | 100000 | WL 4000 L,M FS3 UL1066
| MD 600 | 40000 | WL 4000 F FS3 UL1066
| MD 600 | 85000 | WL 5000 H FS3 UL1066
| MD 600 | 100000 | WL 5000 L,M FS3 UL1066
| MD 600 | 40000 | WL 5000 F FS3 UL1066
| MD 800 | 52000 | WL 2000 FS2 UL489
| MD 800 | 52000 | WL 2500 FS2 UL489
| MD 800 | 52000 | WL 3000 FS2 UL489
| MD 800 | 68000 | WL 4000 FS3 UL489
| MD 800 | 68000 | WL 5000 FS3 UL489
| MD 800 | 65000 | WL 2000 S,H FS2 UL1066
| MD 800 | 85000 | WL 2000 L FS2 UL1066
| MD 800 | 20000 | WL 2000 F FS2 UL1066
| MD 800 | 65000 | WL 3200 S,H FS2 UL1066
| MD 800 | 85000 | WL 3200 L FS2 UL1066
| MD 800 | 100000 | WL 3200 M FS3 UL1066
| MD 800 | 40000 | WL 3200 F FS3 UL1066
| MD 800 | 85000 | WL 4000 H FS3 UL1066
| MD 800 | 100000 | WL 4000 L,M FS3 UL1066
| MD 800 | 40000 | WL 4000 F FS3 UL1066
| MD 800 | 85000 | WL 5000 H FS3 UL1066
| MD 800 | 100000 | WL 5000 L,M FS3 UL1066
| MD 800 | 40000 | WL 5000 F FS3 UL1066
| MG 600 | 52000 | WL 2000 FS2 UL489
| MG 600 | 52000 | WL 2500 FS2 UL489
| MG 600 | 52000 | WL 3000 FS2 UL489
| MG 600 | 68000 | WL 4000 FS3 UL489
| MG 600 | 68000 | WL 5000 FS3 UL489
| MG 600 | 65000 | WL 2000 S,H FS2 UL1066
| MG 600 | 85000 | WL 2000 L FS2 UL1066
| MG 600 | 20000 | WL 2000 F FS2 UL1066
| MG 600 | 65000 | WL 3200 S,H FS2 UL1066
| MG 600 | 85000 | WL 3200 L FS2 UL1066
| MG 600 | 100000 | WL 3200 M FS3 UL1066
| MG 600 | 40000 | WL 3200 F FS3 UL1066
| MG 600 | 85000 | WL 4000 H FS3 UL1066
| MG 600 | 100000 | WL 4000 L,M FS3 UL1066
| MG 600 | 40000 | WL 4000 F FS3 UL1066
| MG 600 | 85000 | WL 5000 H FS3 UL1066
| MG 600 | 100000 | WL 5000 L,M FS3 UL1066
| MG 600 | 40000 | WL 5000 F FS3 UL1066
| MG 800 | 52000 | WL 2500 FS2 UL489
| MG 800 | 52000 | WL 3000 FS2 UL489
| MG 800 | 68000 | WL 4000 FS3 UL489
| MG 800 | 68000 | WL 5000 FS3 UL489
| MG 800 | 65000 | WL 3200 S,H FS2 UL1066
| MG 800 | 85000 | WL 3200 L FS2 UL1066
| MG 800 | 100000 | WL 3200 M FS3 UL1066
| MG 800 | 40000 | WL 3200 F FS3 UL1066
| MG 800 | 85000 | WL 4000 H FS3 UL1066
| MG 800 | 100000 | WL 4000 L,M FS3 UL1066
| MG 800 | 40000 | WL 4000 F FS3 UL1066
| MG 800 | 85000 | WL 5000 H FS3 UL1066
| MG 800 | 100000 | WL 5000 L,M FS3 UL1066
| MG 800 | 40000 | WL 5000 F FS3 UL1066
| SMD 600 s | 9600 | SMD 800 s
| SMD 600 s | 8000 | ND 1200
| SMD 600 s | 8000 | NG 1000
| SMD 600 s | 9600 | NG 1200
| SMD 600 s | 9400 | SND 800 s
| SMD 600 s | 10000 | SND 1000 s
| SMD 600 s | 10000 | SND 1200 s
| SMD 600 s | 7040 | NG 800 s
| SMD 600 s | 8800 | NG 1000 s
| SMD 600 s | 9600 | NG 1200 s
| SMD 600 s | 8000 | PD 1200
| SMD 600 s | 8000 | PD 1600
| SMD 600 s | 9600 | PG 1200
| SMD 600 s | 9600 | PG 1600
| SMD 600 s | 10000 | SPD 1400 s
| SMD 600 s | 10000 | SPD 1600 s
| SMD 600 s | 9600 | PG 1200 s
| SMD 600 s | 7680 | PG 1600 s
| SMD 600 s | 52000 | WL 800 FS1 UL489
| SMD 600 s | 52000 | WL 1200 FS1 UL489
| SMD 600 s | 52000 | WL 800 FS2 UL489
| SMD 600 s | 52000 | WL 1200 FS2 UL489
| SMD 600 s | 52000 | WL 1600 FS2 UL489
| SMD 600 s | 52000 | WL 2000 FS2 UL489
| SMD 600 s | 52000 | WL 2500 FS2 UL489
| SMD 600 s | 52000 | WL 3000 FS2 UL489
| SMD 600 s | 68000 | WL 4000 FS3 UL489
| SMD 600 s | 68000 | WL 5000 FS3 UL489
| SMD 600 s | 50000 | WL 800 N FS2 UL1066
| SMD 600 s | 65000 | WL 800 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 800 L FS2 UL1066
| SMD 600 s | 20000 | WL 800 F FS2 UL1066
| SMD 600 s | 50000 | WL 1600 N FS2 UL1066
| SMD 600 s | 65000 | WL 1600 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 1600 L FS2 UL1066
| SMD 600 s | 20000 | WL 1600 F FS2 UL1066
| SMD 600 s | 65000 | WL 2000 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 2000 L FS2 UL1066
| SMD 600 s | 20000 | WL 2000 F FS2 UL1066
| SMD 600 s | 65000 | WL 3200 S,H FS2 UL1066
| SMD 600 s | 85000 | WL 3200 L FS2 UL1066
| SMD 600 s | 100000 | WL 3200 M FS3 UL1066
| SMD 600 s | 40000 | WL 3200 F FS3 UL1066
| SMD 600 s | 85000 | WL 4000 H FS3 UL1066
| SMD 600 s | 100000 | WL 4000 L,M FS3 UL1066
| SMD 600 s | 40000 | WL 4000 F FS3 UL1066
| SMD 600 s | 85000 | WL 5000 H FS3 UL1066
| SMD 600 s | 100000 | WL 5000 L,M FS3 UL1066
| SMD 600 s | 40000 | WL 5000 F FS3 UL1066
| SMD 800 s | 10000 | SND 1200 s
| SMD 800 s | 9600 | NG 1200 s
| SMD 800 s | 9600 | PG 1200
| SMD 800 s | 9600 | PG 1600
| SMD 800 s | 10000 | SPD 1400 s
| SMD 800 s | 10000 | SPD 1600 s
| SMD 800 s | 9600 | PG 1200 s
| SMD 800 s | 7680 | PG 1600 s
| SMD 800 s | 52000 | WL 1200 FS1 UL489
| SMD 800 s | 52000 | WL 1200 FS2 UL489
| SMD 800 s | 52000 | WL 1600 FS2 UL489
| SMD 800 s | 52000 | WL 2000 FS2 UL489
| SMD 800 s | 52000 | WL 2500 FS2 UL489
| SMD 800 s | 52000 | WL 3000 FS2 UL489
| SMD 800 s | 68000 | WL 4000 FS3 UL489
| SMD 800 s | 68000 | WL 5000 FS3 UL489
| SMD 800 s | 50000 | WL 1600 N FS2 UL1066
| SMD 800 s | 65000 | WL 1600 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 1600 L FS2 UL1066
| SMD 800 s | 20000 | WL 1600 F FS2 UL1066
| SMD 800 s | 65000 | WL 2000 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 2000 L FS2 UL1066
| SMD 800 s | 20000 | WL 2000 F FS2 UL1066
| SMD 800 s | 65000 | WL 3200 S,H FS2 UL1066
| SMD 800 s | 85000 | WL 3200 L FS2 UL1066
| SMD 800 s | 100000 | WL 3200 M FS3 UL1066
| SMD 800 s | 40000 | WL 3200 F FS3 UL1066
| SMD 800 s | 85000 | WL 4000 H FS3 UL1066
| SMD 800 s | 100000 | WL 4000 L,M FS3 UL1066
| SMD 800 s | 40000 | WL 4000 F FS3 UL1066
| SMD 800 s | 85000 | WL 5000 H FS3 UL1066
| SMD 800 s | 100000 | WL 5000 L,M FS3 UL1066
| SMD 800 s | 40000 | WL 5000 F FS3 UL1066
| MG 600 s | 8000 | ND 1200
| MG 600 s | 9600 | NG 1200
| MG 600 s | 10000 | SND 1000 s
| MG 600 s | 10000 | SND 1200 s
| MG 600 s | 8800 | NG 1000 s
| MG 600 s | 9600 | NG 1200 s
| MG 600 s | 8000 | PD 1200
| MG 600 s | 8000 | PD 1600
| MG 600 s | 9600 | PG 1200
| MG 600 s | 9600 | PG 1600
| MG 600 s | 10000 | SPD 1400 s
| MG 600 s | 10000 | SPD 1600 s
| MG 600 s | 9600 | PG 1200 s
| MG 600 s | 7680 | PG 1600 s
| MG 600 s | 52000 | WL 800 FS1 UL489
| MG 600 s | 52000 | WL 1200 FS1 UL489
| MG 600 s | 52000 | WL 800 FS2 UL489
| MG 600 s | 52000 | WL 1200 FS2 UL489
| MG 600 s | 52000 | WL 1600 FS2 UL489
| MG 600 s | 52000 | WL 2000 FS2 UL489
| MG 600 s | 52000 | WL 2500 FS2 UL489
| MG 600 s | 52000 | WL 3000 FS2 UL489
| MG 600 s | 68000 | WL 4000 FS3 UL489
| MG 600 s | 68000 | WL 5000 FS3 UL489
| MG 600 s | 50000 | WL 800 N FS2 UL1066
| MG 600 s | 65000 | WL 800 S,H FS2 UL1066
| MG 600 s | 85000 | WL 800 L FS2 UL1066
| MG 600 s | 20000 | WL 800 F FS2 UL1066
| MG 600 s | 50000 | WL 1600 N FS2 UL1066
| MG 600 s | 65000 | WL 1600 S,H FS2 UL1066
| MG 600 s | 85000 | WL 1600 L FS2 UL1066
| MG 600 s | 20000 | WL 1600 F FS2 UL1066
| MG 600 s | 65000 | WL 2000 S,H FS2 UL1066
| MG 600 s | 85000 | WL 2000 L FS2 UL1066
| MG 600 s | 20000 | WL 2000 F FS2 UL1066
| MG 600 s | 65000 | WL 3200 S,H FS2 UL1066
| MG 600 s | 85000 | WL 3200 L FS2 UL1066
| MG 600 s | 100000 | WL 3200 M FS3 UL1066
| MG 600 s | 40000 | WL 3200 F FS3 UL1066
| MG 600 s | 85000 | WL 4000 H FS3 UL1066
| MG 600 s | 100000 | WL 4000 L,M FS3 UL1066
| MG 600 s | 40000 | WL 4000 F FS3 UL1066
| MG 600 s | 85000 | WL 5000 H FS3 UL1066
| MG 600 s | 100000 | WL 5000 L,M FS3 UL1066
| MG 600 s | 40000 | WL 5000 F FS3 UL1066
| MG 800 s | 10000 | SND 1200 s
| MG 800 s | 8800 | NG 1000 s
| MG 800 s | 9600 | NG 1200 s
| MG 800 s | 8000 | PD 1600
| MG 800 s | 9600 | PG 1600
| MG 800 s | 10000 | SPD 1400 s
| MG 800 s | 10000 | SPD 1600 s
| MG 800 s | 9600 | PG 1200 s
| MG 800 s | 7680 | PG 1600 s
| MG 800 s | 52000 | WL 1200 FS1 UL489
| MG 800 s | 52000 | WL 1200 FS2 UL489
| MG 800 s | 52000 | WL 1600 FS2 UL489
| MG 800 s | 52000 | WL 2000 FS2 UL489
| MG 800 s | 52000 | WL 2500 FS2 UL489
| MG 800 s | 52000 | WL 3000 FS2 UL489
| MG 800 s | 68000 | WL 4000 FS3 UL489
| MG 800 s | 68000 | WL 5000 FS3 UL489
| MG 800 s | 50000 | WL 1600 N FS2 UL1066
| MG 800 s | 65000 | WL 1600 S,H FS2 UL1066
| MG 800 s | 85000 | WL 1600 L FS2 UL1066
| MG 800 s | 20000 | WL 1600 F FS2 UL1066
| MG 800 s | 65000 | WL 2000 S,H FS2 UL1066
| MG 800 s | 85000 | WL 2000 L FS2 UL1066
| MG 800 s | 20000 | WL 2000 F FS2 UL1066
| MG 800 s | 65000 | WL 3200 S,H FS2 UL1066
| MG 800 s | 85000 | WL 3200 L FS2 UL1066
| MG 800 s | 100000 | WL 3200 M FS3 UL1066
| MG 800 s | 40000 | WL 3200 F FS3 UL1066
| MG 800 s | 85000 | WL 4000 H FS3 UL1066
| MG 800 s | 100000 | WL 4000 L,M FS3 UL1066
| MG 800 s | 40000 | WL 4000 F FS3 UL1066
| MG 800 s | 85000 | WL 5000 H FS3 UL1066
| MG 800 s | 100000 | WL 5000 L,M FS3 UL1066
| MG 800 s | 40000 | WL 5000 F FS3 UL1066
| ND 1000 | 52000 | WL 2500 FS2 UL489
| ND 1000 | 52000 | WL 3000 FS2 UL489
| ND 1000 | 68000 | WL 4000 FS3 UL489
| ND 1000 | 68000 | WL 5000 FS3 UL489
| ND 1000 | 65000 | WL 3200 S,H FS2 UL1066
| ND 1000 | 85000 | WL 3200 L FS2 UL1066
| ND 1000 | 100000 | WL 3200 M FS3 UL1066
| ND 1000 | 40000 | WL 3200 F FS3 UL1066
| ND 1000 | 85000 | WL 4000 H FS3 UL1066
| ND 1000 | 100000 | WL 4000 L,M FS3 UL1066
| ND 1000 | 40000 | WL 4000 F FS3 UL1066
| ND 1000 | 85000 | WL 5000 H FS3 UL1066
| ND 1000 | 100000 | WL 5000 L,M FS3 UL1066
| ND 1000 | 40000 | WL 5000 F FS3 UL1066
| ND 1200 | 52000 | WL 2500 FS2 UL489
| ND 1200 | 52000 | WL 3000 FS2 UL489
| ND 1200 | 68000 | WL 4000 FS3 UL489
| ND 1200 | 68000 | WL 5000 FS3 UL489
| ND 1200 | 65000 | WL 3200 S,H FS2 UL1066
| ND 1200 | 85000 | WL 3200 L FS2 UL1066
| ND 1200 | 100000 | WL 3200 M FS3 UL1066
| ND 1200 | 40000 | WL 3200 F FS3 UL1066
| ND 1200 | 85000 | WL 4000 H FS3 UL1066
| ND 1200 | 100000 | WL 4000 L,M FS3 UL1066
| ND 1200 | 40000 | WL 4000 F FS3 UL1066
| ND 1200 | 85000 | WL 5000 H FS3 UL1066
| ND 1200 | 100000 | WL 5000 L,M FS3 UL1066
| ND 1200 | 40000 | WL 5000 F FS3 UL1066
| NG 800 | 52000 | WL 2000 FS2 UL489
| NG 800 | 52000 | WL 2500 FS2 UL489
| NG 800 | 52000 | WL 3000 FS2 UL489
| NG 800 | 68000 | WL 4000 FS3 UL489
| NG 800 | 68000 | WL 5000 FS3 UL489
| NG 800 | 65000 | WL 2000 S,H FS2 UL1066
| NG 800 | 85000 | WL 2000 L FS2 UL1066
| NG 800 | 20000 | WL 2000 F FS2 UL1066
| NG 800 | 65000 | WL 3200 S,H FS2 UL1066
| NG 800 | 85000 | WL 3200 L FS2 UL1066
| NG 800 | 100000 | WL 3200 M FS3 UL1066
| NG 800 | 40000 | WL 3200 F FS3 UL1066
| NG 800 | 85000 | WL 4000 H FS3 UL1066
| NG 800 | 100000 | WL 4000 L,M FS3 UL1066
| NG 800 | 40000 | WL 4000 F FS3 UL1066
| NG 800 | 85000 | WL 5000 H FS3 UL1066
| NG 800 | 100000 | WL 5000 L,M FS3 UL1066
| NG 800 | 40000 | WL 5000 F FS3 UL1066
| NG 1000 | 52000 | WL 2500 FS2 UL489
| NG 1000 | 52000 | WL 3000 FS2 UL489
| NG 1000 | 68000 | WL 4000 FS3 UL489
| NG 1000 | 68000 | WL 5000 FS3 UL489
| NG 1000 | 65000 | WL 3200 S,H FS2 UL1066
| NG 1000 | 85000 | WL 3200 L FS2 UL1066
| NG 1000 | 100000 | WL 3200 M FS3 UL1066
| NG 1000 | 40000 | WL 3200 F FS3 UL1066
| NG 1000 | 85000 | WL 4000 H FS3 UL1066
| NG 1000 | 100000 | WL 4000 L,M FS3 UL1066
| NG 1000 | 40000 | WL 4000 F FS3 UL1066
| NG 1000 | 85000 | WL 5000 H FS3 UL1066
| NG 1000 | 100000 | WL 5000 L,M FS3 UL1066
| NG 1000 | 40000 | WL 5000 F FS3 UL1066
| NG 1200 | 52000 | WL 3000 FS2 UL489
| NG 1200 | 68000 | WL 4000 FS3 UL489
| NG 1200 | 68000 | WL 5000 FS3 UL489
| NG 1200 | 65000 | WL 3200 S,H FS2 UL1066
| NG 1200 | 85000 | WL 3200 L FS2 UL1066
| NG 1200 | 100000 | WL 3200 M FS3 UL1066
| NG 1200 | 40000 | WL 3200 F FS3 UL1066
| NG 1200 | 85000 | WL 4000 H FS3 UL1066
| NG 1200 | 100000 | WL 4000 L,M FS3 UL1066
| NG 1200 | 40000 | WL 4000 F FS3 UL1066
| NG 1200 | 85000 | WL 5000 H FS3 UL1066
| NG 1200 | 100000 | WL 5000 L,M FS3 UL1066
| NG 1200 | 40000 | WL 5000 F FS3 UL1066
| SND 800 s | 9600 | NG 1200 s
| SND 800 s | 9600 | PG 1600
| SND 800 s | 10000 | SPD 1400 s
| SND 800 s | 10000 | SPD 1600 s
| SND 800 s | 9600 | PG 1200 s
| SND 800 s | 7680 | PG 1600 s
| SND 800 s | 52000 | WL 1200 FS1 UL489
| SND 800 s | 52000 | WL 1200 FS2 UL489
| SND 800 s | 52000 | WL 1600 FS2 UL489
| SND 800 s | 52000 | WL 2000 FS2 UL489
| SND 800 s | 52000 | WL 2500 FS2 UL489
| SND 800 s | 52000 | WL 3000 FS2 UL489
| SND 800 s | 68000 | WL 4000 FS3 UL489
| SND 800 s | 68000 | WL 5000 FS3 UL489
| SND 800 s | 50000 | WL 1600 N FS2 UL1066
| SND 800 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 800 s | 85000 | WL 1600 L FS2 UL1066
| SND 800 s | 20000 | WL 1600 F FS2 UL1066
| SND 800 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 800 s | 85000 | WL 2000 L FS2 UL1066
| SND 800 s | 20000 | WL 2000 F FS2 UL1066
| SND 800 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 800 s | 85000 | WL 3200 L FS2 UL1066
| SND 800 s | 100000 | WL 3200 M FS3 UL1066
| SND 800 s | 40000 | WL 3200 F FS3 UL1066
| SND 800 s | 85000 | WL 4000 H FS3 UL1066
| SND 800 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 800 s | 40000 | WL 4000 F FS3 UL1066
| SND 800 s | 85000 | WL 5000 H FS3 UL1066
| SND 800 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 800 s | 40000 | WL 5000 F FS3 UL1066
| SND 1000 s | 10000 | SPD 1400 s
| SND 1000 s | 10000 | SPD 1600 s
| SND 1000 s | 52000 | WL 1600 FS2 UL489
| SND 1000 s | 52000 | WL 2000 FS2 UL489
| SND 1000 s | 52000 | WL 2500 FS2 UL489
| SND 1000 s | 52000 | WL 3000 FS2 UL489
| SND 1000 s | 68000 | WL 4000 FS3 UL489
| SND 1000 s | 68000 | WL 5000 FS3 UL489
| SND 1000 s | 50000 | WL 1600 N FS2 UL1066
| SND 1000 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 1600 L FS2 UL1066
| SND 1000 s | 20000 | WL 1600 F FS2 UL1066
| SND 1000 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 2000 L FS2 UL1066
| SND 1000 s | 20000 | WL 2000 F FS2 UL1066
| SND 1000 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 1000 s | 85000 | WL 3200 L FS2 UL1066
| SND 1000 s | 100000 | WL 3200 M FS3 UL1066
| SND 1000 s | 40000 | WL 3200 F FS3 UL1066
| SND 1000 s | 85000 | WL 4000 H FS3 UL1066
| SND 1000 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 1000 s | 40000 | WL 4000 F FS3 UL1066
| SND 1000 s | 85000 | WL 5000 H FS3 UL1066
| SND 1000 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 1000 s | 40000 | WL 5000 F FS3 UL1066
| SND 1200 s | 52000 | WL 1600 FS2 UL489
| SND 1200 s | 52000 | WL 2000 FS2 UL489
| SND 1200 s | 52000 | WL 2500 FS2 UL489
| SND 1200 s | 52000 | WL 3000 FS2 UL489
| SND 1200 s | 68000 | WL 4000 FS3 UL489
| SND 1200 s | 68000 | WL 5000 FS3 UL489
| SND 1200 s | 50000 | WL 1600 N FS2 UL1066
| SND 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 1600 L FS2 UL1066
| SND 1200 s | 20000 | WL 1600 F FS2 UL1066
| SND 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 2000 L FS2 UL1066
| SND 1200 s | 20000 | WL 2000 F FS2 UL1066
| SND 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| SND 1200 s | 85000 | WL 3200 L FS2 UL1066
| SND 1200 s | 100000 | WL 3200 M FS3 UL1066
| SND 1200 s | 40000 | WL 3200 F FS3 UL1066
| SND 1200 s | 85000 | WL 4000 H FS3 UL1066
| SND 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| SND 1200 s | 40000 | WL 4000 F FS3 UL1066
| SND 1200 s | 85000 | WL 5000 H FS3 UL1066
| SND 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| SND 1200 s | 40000 | WL 5000 F FS3 UL1066
| NG 800 s | 10000 | SPD 1400 s
| NG 800 s | 10000 | SPD 1600 s
| NG 800 s | 52000 | WL 1200 FS1 UL489
| NG 800 s | 52000 | WL 1200 FS2 UL489
| NG 800 s | 52000 | WL 1600 FS2 UL489
| NG 800 s | 52000 | WL 2000 FS2 UL489
| NG 800 s | 52000 | WL 2500 FS2 UL489
| NG 800 s | 52000 | WL 3000 FS2 UL489
| NG 800 s | 68000 | WL 4000 FS3 UL489
| NG 800 s | 68000 | WL 5000 FS3 UL489
| NG 800 s | 50000 | WL 1600 N FS2 UL1066
| NG 800 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 800 s | 85000 | WL 1600 L FS2 UL1066
| NG 800 s | 20000 | WL 1600 F FS2 UL1066
| NG 800 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 800 s | 85000 | WL 2000 L FS2 UL1066
| NG 800 s | 20000 | WL 2000 F FS2 UL1066
| NG 800 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 800 s | 85000 | WL 3200 L FS2 UL1066
| NG 800 s | 100000 | WL 3200 M FS3 UL1066
| NG 800 s | 40000 | WL 3200 F FS3 UL1066
| NG 800 s | 85000 | WL 4000 H FS3 UL1066
| NG 800 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 800 s | 40000 | WL 4000 F FS3 UL1066
| NG 800 s | 85000 | WL 5000 H FS3 UL1066
| NG 800 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 800 s | 40000 | WL 5000 F FS3 UL1066
| NG 1000 s | 52000 | WL 1600 FS2 UL489
| NG 1000 s | 52000 | WL 2000 FS2 UL489
| NG 1000 s | 52000 | WL 2500 FS2 UL489
| NG 1000 s | 52000 | WL 3000 FS2 UL489
| NG 1000 s | 68000 | WL 4000 FS3 UL489
| NG 1000 s | 68000 | WL 5000 FS3 UL489
| NG 1000 s | 50000 | WL 1600 N FS2 UL1066
| NG 1000 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 1600 L FS2 UL1066
| NG 1000 s | 20000 | WL 1600 F FS2 UL1066
| NG 1000 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 2000 L FS2 UL1066
| NG 1000 s | 20000 | WL 2000 F FS2 UL1066
| NG 1000 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 1000 s | 85000 | WL 3200 L FS2 UL1066
| NG 1000 s | 100000 | WL 3200 M FS3 UL1066
| NG 1000 s | 40000 | WL 3200 F FS3 UL1066
| NG 1000 s | 85000 | WL 4000 H FS3 UL1066
| NG 1000 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 1000 s | 40000 | WL 4000 F FS3 UL1066
| NG 1000 s | 85000 | WL 5000 H FS3 UL1066
| NG 1000 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 1000 s | 40000 | WL 5000 F FS3 UL1066
| NG 1200 s | 52000 | WL 1600 FS2 UL489
| NG 1200 s | 52000 | WL 2000 FS2 UL489
| NG 1200 s | 52000 | WL 2500 FS2 UL489
| NG 1200 s | 52000 | WL 3000 FS2 UL489
| NG 1200 s | 68000 | WL 4000 FS3 UL489
| NG 1200 s | 68000 | WL 5000 FS3 UL489
| NG 1200 s | 50000 | WL 1600 N FS2 UL1066
| NG 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 1600 L FS2 UL1066
| NG 1200 s | 20000 | WL 1600 F FS2 UL1066
| NG 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 2000 L FS2 UL1066
| NG 1200 s | 20000 | WL 2000 F FS2 UL1066
| NG 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| NG 1200 s | 85000 | WL 3200 L FS2 UL1066
| NG 1200 s | 100000 | WL 3200 M FS3 UL1066
| NG 1200 s | 40000 | WL 3200 F FS3 UL1066
| NG 1200 s | 85000 | WL 4000 H FS3 UL1066
| NG 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| NG 1200 s | 40000 | WL 4000 F FS3 UL1066
| NG 1200 s | 85000 | WL 5000 H FS3 UL1066
| NG 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| NG 1200 s | 40000 | WL 5000 F FS3 UL1066
| PD 1200 | 52000 | WL 2500 FS2 UL489
| PD 1200 | 52000 | WL 3000 FS2 UL489
| PD 1200 | 68000 | WL 4000 FS3 UL489
| PD 1200 | 68000 | WL 5000 FS3 UL489
| PD 1200 | 65000 | WL 3200 S,H FS2 UL1066
| PD 1200 | 85000 | WL 3200 L FS2 UL1066
| PD 1200 | 100000 | WL 3200 M FS3 UL1066
| PD 1200 | 40000 | WL 3200 F FS3 UL1066
| PD 1200 | 85000 | WL 4000 H FS3 UL1066
| PD 1200 | 100000 | WL 4000 L,M FS3 UL1066
| PD 1200 | 40000 | WL 4000 F FS3 UL1066
| PD 1200 | 85000 | WL 5000 H FS3 UL1066
| PD 1200 | 100000 | WL 5000 L,M FS3 UL1066
| PD 1200 | 40000 | WL 5000 F FS3 UL1066
| PD 1600 | 68000 | WL 4000 FS3 UL489
| PD 1600 | 68000 | WL 5000 FS3 UL489
| PD 1600 | 65000 | WL 3200 S,H FS2 UL1066
| PD 1600 | 85000 | WL 3200 L FS2 UL1066
| PD 1600 | 100000 | WL 3200 M FS3 UL1066
| PD 1600 | 40000 | WL 3200 F FS3 UL1066
| PD 1600 | 85000 | WL 4000 H FS3 UL1066
| PD 1600 | 100000 | WL 4000 L,M FS3 UL1066
| PD 1600 | 40000 | WL 4000 F FS3 UL1066
| PD 1600 | 85000 | WL 5000 H FS3 UL1066
| PD 1600 | 100000 | WL 5000 L,M FS3 UL1066
| PD 1600 | 40000 | WL 5000 F FS3 UL1066
| PG 1200 | 52000 | WL 3000 FS2 UL489
| PG 1200 | 68000 | WL 4000 FS3 UL489
| PG 1200 | 68000 | WL 5000 FS3 UL489
| PG 1200 | 65000 | WL 3200 S,H FS2 UL1066
| PG 1200 | 85000 | WL 3200 L FS2 UL1066
| PG 1200 | 100000 | WL 3200 M FS3 UL1066
| PG 1200 | 40000 | WL 3200 F FS3 UL1066
| PG 1200 | 85000 | WL 4000 H FS3 UL1066
| PG 1200 | 100000 | WL 4000 L,M FS3 UL1066
| PG 1200 | 40000 | WL 4000 F FS3 UL1066
| PG 1200 | 85000 | WL 5000 H FS3 UL1066
| PG 1200 | 100000 | WL 5000 L,M FS3 UL1066
| PG 1200 | 40000 | WL 5000 F FS3 UL1066
| PG 1600 | 68000 | WL 4000 FS3 UL489
| PG 1600 | 68000 | WL 5000 FS3 UL489
| PG 1600 | 85000 | WL 4000 H FS3 UL1066
| PG 1600 | 100000 | WL 4000 L,M FS3 UL1066
| PG 1600 | 40000 | WL 4000 F FS3 UL1066
| PG 1600 | 85000 | WL 5000 H FS3 UL1066
| PG 1600 | 100000 | WL 5000 L,M FS3 UL1066
| PG 1600 | 40000 | WL 5000 F FS3 UL1066
| SPD 1400 s | 52000 | WL 2000 FS2 UL489
| SPD 1400 s | 52000 | WL 2500 FS2 UL489
| SPD 1400 s | 52000 | WL 3000 FS2 UL489
| SPD 1400 s | 68000 | WL 4000 FS3 UL489
| SPD 1400 s | 68000 | WL 5000 FS3 UL489
| SPD 1400 s | 65000 | WL 2000 S,H FS2 UL1066
| SPD 1400 s | 85000 | WL 2000 L FS2 UL1066
| SPD 1400 s | 20000 | WL 2000 F FS2 UL1066
| SPD 1400 s | 65000 | WL 3200 S,H FS2 UL1066
| SPD 1400 s | 85000 | WL 3200 L FS2 UL1066
| SPD 1400 s | 100000 | WL 3200 M FS3 UL1066
| SPD 1400 s | 40000 | WL 3200 F FS3 UL1066
| SPD 1400 s | 85000 | WL 4000 H FS3 UL1066
| SPD 1400 s | 100000 | WL 4000 L,M FS3 UL1066
| SPD 1400 s | 40000 | WL 4000 F FS3 UL1066
| SPD 1400 s | 85000 | WL 5000 H FS3 UL1066
| SPD 1400 s | 100000 | WL 5000 L,M FS3 UL1066
| SPD 1400 s | 40000 | WL 5000 F FS3 UL1066
| SPD 1600 s | 52000 | WL 2000 FS2 UL489
| SPD 1600 s | 52000 | WL 2500 FS2 UL489
| SPD 1600 s | 52000 | WL 3000 FS2 UL489
| SPD 1600 s | 68000 | WL 4000 FS3 UL489
| SPD 1600 s | 68000 | WL 5000 FS3 UL489
| SPD 1600 s | 65000 | WL 2000 S,H FS2 UL1066
| SPD 1600 s | 85000 | WL 2000 L FS2 UL1066
| SPD 1600 s | 20000 | WL 2000 F FS2 UL1066
| SPD 1600 s | 65000 | WL 3200 S,H FS2 UL1066
| SPD 1600 s | 85000 | WL 3200 L FS2 UL1066
| SPD 1600 s | 100000 | WL 3200 M FS3 UL1066
| SPD 1600 s | 40000 | WL 3200 F FS3 UL1066
| SPD 1600 s | 85000 | WL 4000 H FS3 UL1066
| SPD 1600 s | 100000 | WL 4000 L,M FS3 UL1066
| SPD 1600 s | 40000 | WL 4000 F FS3 UL1066
| SPD 1600 s | 85000 | WL 5000 H FS3 UL1066
| SPD 1600 s | 100000 | WL 5000 L,M FS3 UL1066
| SPD 1600 s | 40000 | WL 5000 F FS3 UL1066
| PG 1200 s | 52000 | WL 1600 FS2 UL489
| PG 1200 s | 52000 | WL 2000 FS2 UL489
| PG 1200 s | 52000 | WL 2500 FS2 UL489
| PG 1200 s | 52000 | WL 3000 FS2 UL489
| PG 1200 s | 68000 | WL 4000 FS3 UL489
| PG 1200 s | 68000 | WL 5000 FS3 UL489
| PG 1200 s | 50000 | WL 1600 N FS2 UL1066
| PG 1200 s | 65000 | WL 1600 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 1600 L FS2 UL1066
| PG 1200 s | 20000 | WL 1600 F FS2 UL1066
| PG 1200 s | 65000 | WL 2000 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 2000 L FS2 UL1066
| PG 1200 s | 20000 | WL 2000 F FS2 UL1066
| PG 1200 s | 65000 | WL 3200 S,H FS2 UL1066
| PG 1200 s | 85000 | WL 3200 L FS2 UL1066
| PG 1200 s | 100000 | WL 3200 M FS3 UL1066
| PG 1200 s | 40000 | WL 3200 F FS3 UL1066
| PG 1200 s | 85000 | WL 4000 H FS3 UL1066
| PG 1200 s | 100000 | WL 4000 L,M FS3 UL1066
| PG 1200 s | 40000 | WL 4000 F FS3 UL1066
| PG 1200 s | 85000 | WL 5000 H FS3 UL1066
| PG 1200 s | 100000 | WL 5000 L,M FS3 UL1066
| PG 1200 s | 40000 | WL 5000 F FS3 UL1066
| PG 1600 s | 52000 | WL 2500 FS2 UL489
| PG 1600 s | 52000 | WL 3000 FS2 UL489
| PG 1600 s | 68000 | WL 4000 FS3 UL489
| PG 1600 s | 68000 | WL 5000 FS3 UL489
| PG 1600 s | 65000 | WL 3200 S,H FS2 UL1066
| PG 1600 s | 85000 | WL 3200 L FS2 UL1066
| PG 1600 s | 100000 | WL 3200 M FS3 UL1066
| PG 1600 s | 40000 | WL 3200 F FS3 UL1066
| PG 1600 s | 85000 | WL 4000 H FS3 UL1066
| PG 1600 s | 100000 | WL 4000 L,M FS3 UL1066
| PG 1600 s | 40000 | WL 4000 F FS3 UL1066
| PG 1600 s | 85000 | WL 5000 H FS3 UL1066
| PG 1600 s | 100000 | WL 5000 L,M FS3 UL1066
| PG 1600 s | 40000 | WL 5000 F FS3 UL1066
| WL 800 FS1 UL489 | 52000 | WL 1200 FS1 UL489
| WL 800 FS1 UL489 | 52000 | WL 1200 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 1600 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 2000 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 2500 FS2 UL489
| WL 800 FS1 UL489 | 52000 | WL 3000 FS2 UL489
| WL 800 FS1 UL489 | 68000 | WL 4000 FS3 UL489
| WL 800 FS1 UL489 | 68000 | WL 5000 FS3 UL489
| WL 800 FS1 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 800 FS1 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 800 FS1 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 800 FS1 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 FS1 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 800 FS1 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 800 FS1 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 800 FS1 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 800 FS1 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 800 FS1 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 FS1 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1200 FS1 UL489 | 52000 | WL 1600 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1200 FS1 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1200 FS1 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1200 FS1 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1200 FS1 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 1200 FS1 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1200 FS1 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1200 FS1 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1200 FS1 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1200 FS1 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1200 FS1 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 800 FS2 UL489 | 52000 | WL 1200 FS1 UL489
| WL 800 FS2 UL489 | 52000 | WL 1200 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 1600 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 800 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 800 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 800 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 800 FS2 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 800 FS2 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 800 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 800 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 800 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 800 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 800 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 800 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 800 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1200 FS2 UL489 | 52000 | WL 1600 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1200 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1200 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1200 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1200 FS2 UL489 | 50000 | WL 1600 N FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 1600 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 1600 L FS2 UL1066
| WL 1200 FS2 UL489 | 20000 | WL 1600 F FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1200 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1200 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1200 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1200 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1200 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 FS2 UL489 | 52000 | WL 2000 FS2 UL489
| WL 1600 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 1600 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 1600 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 1600 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 1600 FS2 UL489 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 FS2 UL489 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 FS2 UL489 | 52000 | WL 2500 FS2 UL489
| WL 2000 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 2000 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 2000 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 2000 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 2500 FS2 UL489 | 52000 | WL 3000 FS2 UL489
| WL 2500 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 2500 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 2500 FS2 UL489 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 3200 L FS2 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 3200 M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 3200 F FS3 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 2500 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 2500 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2500 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 3000 FS2 UL489 | 68000 | WL 4000 FS3 UL489
| WL 3000 FS2 UL489 | 68000 | WL 5000 FS3 UL489
| WL 3000 FS2 UL489 | 85000 | WL 4000 H FS3 UL1066
| WL 3000 FS2 UL489 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3000 FS2 UL489 | 40000 | WL 4000 F FS3 UL1066
| WL 3000 FS2 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 3000 FS2 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3000 FS2 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 FS3 UL489 | 68000 | WL 5000 FS3 UL489
| WL 4000 FS3 UL489 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 FS3 UL489 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 FS3 UL489 | 40000 | WL 5000 F FS3 UL1066
| WL 5000 FS3 UL489 |  | na
| WL 800 N FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 N FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 N FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 N FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 N FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 N FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 N FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 N FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 N FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 N FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 N FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 S,H FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 L FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 L FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 L FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 L FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 800 F FS2 UL1066 | 52000 | WL 1200 FS1 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 1200 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 1600 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 800 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 800 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 800 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 800 F FS2 UL1066 | 50000 | WL 1600 N FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 1600 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 1600 L FS2 UL1066
| WL 800 F FS2 UL1066 | 20000 | WL 1600 F FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 800 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 800 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 800 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 800 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 800 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 N FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 N FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 N FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 N FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 N FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 N FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 N FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 N FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 N FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 N FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 S,H FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 L FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 L FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 52000 | WL 2000 FS2 UL489
| WL 1600 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 1600 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 1600 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 1600 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 1600 F FS2 UL1066 | 65000 | WL 2000 S,H FS2 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 2000 L FS2 UL1066
| WL 1600 F FS2 UL1066 | 20000 | WL 2000 F FS2 UL1066
| WL 1600 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 1600 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 1600 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 1600 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 S,H FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 S,H FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 L FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 L FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 52000 | WL 2500 FS2 UL489
| WL 2000 F FS2 UL1066 | 52000 | WL 3000 FS2 UL489
| WL 2000 F FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 2000 F FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 2000 F FS2 UL1066 | 65000 | WL 3200 S,H FS2 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 3200 L FS2 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 3200 M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 3200 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 2000 F FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 2000 F FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 2000 F FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 S,H FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 S,H FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 S,H FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 L FS2 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 L FS2 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 L FS2 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 L FS2 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 L FS2 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 L FS2 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 L FS2 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 L FS2 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 M FS3 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 M FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 M FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 M FS3 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 M FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 M FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 M FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 M FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 3200 F FS3 UL1066 | 68000 | WL 4000 FS3 UL489
| WL 3200 F FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 3200 F FS3 UL1066 | 85000 | WL 4000 H FS3 UL1066
| WL 3200 F FS3 UL1066 | 100000 | WL 4000 L,M FS3 UL1066
| WL 3200 F FS3 UL1066 | 40000 | WL 4000 F FS3 UL1066
| WL 3200 F FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 3200 F FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 3200 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 H FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 H FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 H FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 H FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 L,M FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 L,M FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 4000 F FS3 UL1066 | 68000 | WL 5000 FS3 UL489
| WL 4000 F FS3 UL1066 | 85000 | WL 5000 H FS3 UL1066
| WL 4000 F FS3 UL1066 | 100000 | WL 5000 L,M FS3 UL1066
| WL 4000 F FS3 UL1066 | 40000 | WL 5000 F FS3 UL1066
| WL 5000 H FS3 UL1066 |  | na
| WL 5000 L,M FS3 UL1066 |  | na
| WL 5000 F FS3 UL1066 |  | na