## Main Sheet
Jignesh.Parmar www.electricalnotes.wordpress.com
LT Bus
|  | 3000 |  | 8000 |  |  | 12000 |  | 12000 |  |  | 12000 |  |  |  | 12000 |  |  | 12000 |  |  | 12000 |  |  |  | 12000 |  |  | 12000 |  |  | 12000 |  |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000 |  | 12000
|  | 3000 Mtr |  | 5000 Mtr |  |  | 4000 Mtr |  | Mtr |  |  | Mtr |  |  |  | Mtr |  |  | Mtr |  |  | Mtr |  |  |  | Mtr |  |  | Mtr |  |  | Mtr |  |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr |  | Mtr
|  | - | A |  |  | B |  | C |  |  | D |  |  |  | E |  |  | F |  |  | G |  |  |  | H |  |  | I |  |  | J |  |  | K |  | L |  | M |  | N |  | O |  | P |  | Q |  | R |  | S |  | T |  | U | 1Ph
3Ph
|  |  | Load -A |  |  | Load -B |  | Load -C |  |  | Load -D |  |  |  | Load -E |  |  | Load -F |  |  | Load -G |  |  |  | Load -H |  |  | Load -I |  |  | Load -J |  |  | Load -K |  | Load -L |  | Load -M |  | Load -N |  | Load -O |  | Load -P |  | Load -Q |  | Load -R |  | Load -S |  | Load -T |  | Load -U
Convert Your Distribution system in to single Line Diagaram and then Enter Following Detail
Sending End Voltage |  |  |  |  | 33000 |  | Volt | % VOLTAGE REGULATION
|  | Load |  |  | Load Detail |  |  | 1Ph/ 3Ph |  | KW | P.F |  | Distance (Mtr) |  |  |  | Conductor |  |  | Code |  |  | Size |  |  |  | Load Amp | Conductor Amp |  | No of Cond / Phase | Voltage Drop (V) |  | Reciving Voltge |  | %VR | Result
[13 empty] | From-To |  |  | Meter
| 1.732 | Load -A |  |  | XYZ |  |  | 3Ph |  | 800 | 0.8 |  | - | To | A | 3000 | ACSR |  |  | DOG |  |  | Al (6 /4.72 ),GI(7 /1.57 ) |  |  |  | 17.496 | 325 |  | 1 | 46.5418 |  | 32953.4582 |  | 0.1412% | O.K | 1
| 1.732 | Load -B | [5 empty] | 3Ph |  | 4000 | 0.8 |  | A | To | B | 5000 | ACSR |  |  | DOG |  |  | Al (6 /4.72 ),GI(7 /1.57 ) |  |  |  | 87.4799 | 325 |  | 1 | 620.5576 |  | 32379.4424 |  | 1.917% | O.K | 1
| 1.732 | Load -C | [5 empty] | 3Ph |  | 4000 | 0.8 |  | B | To | C | 4000 | ACSR |  |  | DOG |  |  | Al (6 /4.72 ),GI(7 /1.57 ) |  |  |  | 87.4799 | 325 |  | 1 | 930.8364 |  | 32069.1636 |  | 2.903% | O.K | 1
| 1 | Load -D | [10 empty] | C | To | D | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -E | [10 empty] | D | To | E | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -F | [10 empty] | E | To | F | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -G | [10 empty] | F | To | G | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -H | [10 empty] | G | To | H | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -I | [10 empty] | H | To | I | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -J | [10 empty] | I | To | J | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -K | [10 empty] | J | To | K | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -L | [10 empty] | K | To | L | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -M | [10 empty] | L | To | M | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -N | [10 empty] | M | To | N | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -O | [10 empty] | N | To | O | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -P | [10 empty] | O | To | P | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -Q | [10 empty] | P | To | Q | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -R | [10 empty] | Q | To | R | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -S | [10 empty] | R | To | S | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -T | [10 empty] | S | To | T | [11 empty] | 0 | [5 empty] | 0 |  | 0%
| 1 | Load -U | [10 empty] | T | To | U | [11 empty] | 0 | [5 empty] | 0 |  | 0%
|  | TOTAL % Voltage Regulation of Line | [13 empty] | 12000 | [14 empty] | 1597.9358 |  |  |  | 4.96%
Add Conductor Detail
Calculation of % Voltage Drop of Overhead Line

## Conductor Detail
Conductor | ACSR | ACSR(Aluminum conductor with Steel Rainforce) | [13 empty] | Conductor | AAAC | AAAC (All Aluminum Alloy Conductor) |  |  |  |  | Conductor | AAC | AAC (All Aluminum Conductor)
CODE WORD | Aluminum Area Sq mm |  | Total Sectional Area (Sq mm) | Stranding and Wire Diameter |  |  |  | Overall Dia. (mm) appro | WEIGHT MASS |  |  | Resistance at 20 degC Ohms/Km (MAX) | Reactance at 20 degC Ohms/Km (MAX) | Current Rating (Amps) | Ultimate Breaking Load (KN) | CODE WORD | Conductor (AL) |  | Overall Dia. (mm) appro | Resistance at 20 degC Ohms/Km (MAX) | Reactance at 20 degC Ohms/Km (MAX) | Current Rating (Amps) | CODE WORD | Conductor (AL) |  | Overall Dia. (mm) appro | Resistance at 20 degC Ohms/Km (MAX) | Reactance at 20 degC Ohms/Km (MAX) | Current Rating (Amps)
|  |  |  | Conductor (AL) |  | Conductor (ST) |  |  | Total | AL. | ST.
| Nominal | Sectional |  | NO. | DIA (mm) | NO | DIA (mm) |  | Kg/Km | Kg/Km | Kg/Km | [5 empty] | NO. | DIA (mm) | [5 empty] | NO. | DIA (mm)
MOLE | 10 | 10.60 | 12.37 | 6 | 1.50 | - | 1.50 | 4.50 | 43 | 29 | 14 | 2.78 |  | 67 | 3.97 | Akron | 7 | .198 | .0240 | 0.785 |  | 107 | Peachbell | 7 | .0612 | .184 | 0.805 |  | 103 | ACSR | ACSR | DOG | 6 | 4.72 | 7 | 1.57 | Al (6 /4.72 ),GI(7 /1.57 ) | 0.3182 | 0.429 | 0.8 | 0.6 | 0.51196 | 325
ROSE | 18 | 18.10 | 21.12 | 6 | 1.96 | 1 | 1.96 | 5.88 | 73 | 49.5 | 23.5 | 1.618 |  | 104 | 6.74 | Alton | 7 | .250 | .0382 | 0.493 |  | 143 | Rose | 7 | .0772 | .232 | 0.506 |  | 138 | AAAC | ACSR | DOG | 6 | 4.72 | 7 | 1.57 | Al (6 /4.72 ),GI(7 /1.57 ) | 0.3182 | 0.429 | 0.8 | 0.6 | 0.51196 | 325
SQUIRREL | 20 | 20.98 | 24.48 | 6 | 2.11 | 1 | 2.11 | 6.33 | 85 | 58 | 27 | 1.394 |  | 76 | 7.61 | Ames | 7 | .316 | .0608 | 0.31 |  | 191 | Iris | 7 | .0924 | .292 | 0.318 |  | 185 | AAC | ACSR | DOG | 6 | 4.72 | 7 | 1.57 | Al (6 /4.72 ),GI(7 /1.57 ) | 0.3182 | 0.429 | 0.8 | 0.6 | 0.51196 | 325
WEASEL | 30 | 31.61 | 36.88 | 6 | 2.59 | 1 | 2.59 | 7.77 | 128 | 87 | 41 | 0.9289 |  | 95 | 11.12 | Azusa | 7 | .398 | .0968 | 0.195 |  | 256 | Pansy | 7 | .1903 | .328 | 0.252 |  | 214 | [10 empty] | 0 | 1 | 0
RABBIT | 50 | 52.88 | 61.70 | 6 | 3.35 | 1 | 3.53 | 10.05 | 214 | 145 | 69 | 0.5524 |  | 135 | 18.25 | Anaheim | 7 | .447 | .1221 | 0.154 |  | 296 | Poppy | 7 | .1228 | .368 | 0.2 |  | 247 | [10 empty] | 0 | 1 | 0
RACOON | 80 | 78.83 | 91.97 | 6 | 4.09 | 1 | 4.09 | 12.27 | 318 | 215 | 103 | 0.3712 |  | 180 | 26.91 | Amherst | 7 | .502 | .1537 | 0.123 |  | 342 | Aster | 7 | .1379 | .414 | 0.159 |  | 286 | [10 empty] | 0 | 1 | 0
DOG | 100 | 105.0 | 118.5 | 6 | 4.72 | 7 | 1.57 | 14.15 | 394 | 288.3 | 105.7 | 0.3182 | 0.429 | 325 | 32.41 | Alliance | 7 | .563 | .1939 | 0.0973 |  | 395 | Phlox | 7 | .1548 | .464 | 0.126 |  | 331 | [10 empty] | 0 | 1 | 0
WOLF | 150 | 158.1 | 194.9 | 30 | 2.59 | 7 | 2.59 | 18.13 | 727 | 438 | 289 | 0.1871 |  | 305 | 67.34 | Butte | 19 | .642 | .2456 | 0.0769 |  | 460 | OxIiP | 7 | .1739 | .522 | 0.0999 |  | 383 | [10 empty] | 0 | 1 | 0
PANTHER | 200 | 212.1 | 261.5 | 30 | 3.00 | 7 | 3.00 | 21.00 | 976 | 588.5 | 387.5 | 0.139 |  | 370 | 89.67 | Canton | 19 | .721 | .3098 | 0.061 |  | 532 | Sneezewort | 7 | .1890 | .567 | 0.0846 |  | 425 | [10 empty] | 0 | 1 | 0
ZEBRA | 420 | 428.9 | 484.5 | 54 | 3.18 | 7 | 3.18 | 28.62 | 1621 | 1182 | 439 | 0.06868 |  | 635 | 130.32 | Cairo | 19 | .783 | .3655 | 0.0518 |  | 590 | Valerian | 7 | .1147 | .574 | 0.0846 |  | 426 | [10 empty] | 0 | 1 | 0
MOOSE | 520 | 528.5 | 597.0 | 54 | 3.53 | 7 | 3.53 | 31.77 | 1998 | 1463 | 535 | 0.05595 |  | 763 | 159.60 | Darien | 19 | .858 | .4394 | 0.0431 |  | 663 | Daisy | 7 | .1953 | .586 | 0.0793 |  | 443 | [10 empty] | 0 | 1 | 0
GOPHER | 16 | 25.90 | 30.62 | 6 | 2.36 | 1 | 2.36 | 7.08 | 106 | 72 | 34 | 1.098 |  | 85 | 952 | Elgin | 19 | .927 | .5124 | 0.0371 |  | 729 | Laurel | 19 | .1185 | .593 | 0.0793 |  | 444 | [10 empty] | 0 | 1 | 0
FERRET | 25 | 41.87 | 49.98 | 6 | 3.00 | 1 | 3 | 9 | 171 | 116 | 55 | 0.6795 |  | 115 | 1503 | Flint | 37 | .991 | .5818 | 0.0327 |  | 790 | Peony | 19 | .1257 | .629 | 0.0706 |  | 478 | [10 empty] | 0 | 1 | 0
MINK | 40 | 63.32 | 73.65 | 6 | 3.66 | 1 | 3.66 | 10.98 | 255 | 173 | 82 | 0.4565 |  | 165 | 2207 | Greely | 37 | 1.108 | .7282 | 0.0263 |  | 908 | Tulip | 19 | .1331 | .666 | 0.063 |  | 513 | [10 empty] | 0 | 1 | 0
HORSE | 42 | 71.58 | 116.20 | 12 | 2.75 | 7 | 2.79 | 13.95 | 542 | 204 | 338 | 0.3977 |  | 268 | 6108 | [7 empty] | Daffodil | 19 | .1357 | .679 | 0.0605 |  | 526 | [10 empty] | 0 | 1 | 0
BEAVER | 45 | 74.07 | 87.53 | 6 | 3.99 | 1 | 3.99 | 11.97 | 303 | 205 | 98 | 0.3841 |  | 176 | 2613 | [7 empty] | Canna | 19 | .1447 | .724 | 0.0534 |  | 570 | [10 empty] | 0 | 1 | 0
OTTER | 50 | 82.85 | 97.91 | 6 | 4.22 | 1 | 4.22 | 12.66 | 339 | 230 | 109 | 0.3434 |  | 185 | 2923 | [7 empty] | Goldentuft | 19 | .1538 | .769 | 0.0472 |  | 616 | [10 empty] | 0 | 1 | 0
CAT | 55 | 94.21 | 111.30 | 6 | 4.5 | 7 | 4.50 | 13.50 | 385 | 261 | 124 | 0.302 |  | 195 | 3324 | [7 empty] | Cosmos | 19 | .1584 | .793 | 0.0445 |  | 639 | [10 empty] | 0 | 1 | 0
LEOPARD | 80 | 129.70 | 148.40 | 6 | 5.28 | 7 | 1.76 | 15.48 | 493 | 360 | 133 | 0.2193 |  | 275 | 4137 | [7 empty] | Syringa | 37 | .1135 | .795 | 0.0445 |  | 639 | [10 empty] | 0 | 1 | 0
COYOTE | 80 | 128.50 | 151.60 | 26 | 2.54 | 7 | 1.90 | 15.86 | 521 | 365 | 156 | 0.2214 |  | 260 | 4638 | [7 empty] | Zinnia | 19 | .1622 | .811 | 0.0425 |  | 658 | [10 empty] | 0 | 1 | 0
TIGER | 80 | 128.10 | 161.80 | 30 | 2.36 | 7 | 2.36 | 16.52 | 604 | 363 | 241 | 0.2221 |  | 265 | 5758 | [7 empty] | Hyacinth | 37 | .1162 | .813 | 0.0425 |  | 658 | [10 empty] | 0 | 1 | 0
LYNX | 110 | 179.00 | 226.20 | 30 | 2.79 | 7 | 2.79 | 19.53 | 844 | 506 | 338 | 0.1589 |  | 335 | 7950 | [7 empty] | Dahlia | 19 | .1711 | .856 | 0.0382 |  | 703
LION | 140 | 232.50 | 293.90 | 30 | 3.18 | 7 | 3.18 | 22.26 | 1097 | 659 | 438 | 0.1223 |  | 405 | 10210 | [7 empty] | Mistletoe | 37 | .1226 | .858 | 0.0382 |  | 704
BEAR | 160 | 258.10 | 326.10 | 30 | 3.35 | 7 | 3.35 | 23.45 | 1219 | 734 | 485 | 0.1102 |  | 430 | 11310 | [7 empty] | Meadowsweet | 37 | .1273 | .891 | 0.0355 |  | 738
GOAT | 185 | 316.5 | 400 | 30 | 3.71 | 7 | 3.71 | 25.97 | 1492 | 896 | 596 | 0.0898 |  | 542 | 13780 | [7 empty] | Orchid | 37 | .1311 | .918 | 0.0335 |  | 765
SHEEP | 225 | 366.1 | 462.6 | 30 | 3.99 | 7 | 3.99 | 27.93 | 1726 | 1036 | 690 | 0.0777 |  | 592 | 15910 | [7 empty] | Heuchera | 37 | .1326 | .928 | 0.0328 |  | 775
DEER | 260 | 419.3 | 529.8 | 30 | 4.27 | 7 | 4.27 | 29.89 | 1977 | 1188 | 789 | 0.0678 |  | 639 | 18230 | [7 empty] | Verbena | 37 | .1375 | .963 | 0.0305 |  | 812
FLK | 300 | 465.7 | 588.4 | 30 | 4.5 | 7 | 4.5 | 31.5 | 2196 | 1320 | 876 | 0.0611 |  | 679 | 20240 | [7 empty] | Flag | 61 | .1071 | .964 | 0.0305 |  | 812
CAMEL | 300 | 464.5 | 537.7 | 54 | 3.35 | 7 | 3.35 | 30.15 | 1804 | 1318 | 486 | 0.0612 |  | 677 | 14750 | [7 empty] | Violet | 37 | .1391 | .974 | 0.0299 |  | 823
SPARROW | 20 | 33.16 | 39.22 | 6 | 2.67 | 7 | 2.67 | 8.01 | 135 | 92 | 43 | 0.8578 |  | 139 | 1208 | [7 empty] | Nasturtium | 61 | .1083 | .975 | 0.0299 |  | 823
FOX | 22 | 36.21 | 42.92 | 6 | 2.79 | 7 | 2.79 | 8.37 | 149 | 101 | 48 | 0.7857 |  | 147 | 1313 | [7 empty] | Petunia | 37 | .1424 | .997 | 0.0286 |  | 847
GUINEA | 49 | 78.56 | 127.2 | 12 | 2.92 | 7 | 2.92 | 14.6 | 590 | 224 | 366 | 0.362 |  | 244 | 6664 | [7 empty] | Cattail | 61 | .1109 | .998 | 0.0286 |  | 847
LARK | 125 | 196.1 | 247.8 | 30 | 2.92 | 7 | 2.92 | 20.44 | 922 | 556 | 366 | 0.1451 |  | 410 | 8559 | [7 empty] | Arbutus | 37 | .1446 | 1.026 | 0.0271 |  | 878
[23 empty] | Lilac | 61 | .1142 | 1.028 | 0.027 |  | 879
[23 empty] | Cockscomb | 37 | .1560 | 1.092 | 0.0239 |  | 948
[23 empty] | Snapdragon | 61 | .1215 | 1.094 | 0.0239 |  | 948
[23 empty] | Magnolia | 37 | .1606 | 1.124 | 0.0226 |  | 982
[23 empty] | Goldenrod | 61 | .1251 | 1.126 | 0.0226 |  | 983
[23 empty] | Hawkweed | 37 | .1644 | 1.150 | 0.0216 |  | 1010
[23 empty] | Camellia | 61 | .1280 | 1.152 | 0.0216 |  | 1011
[23 empty] | Bluebell | 37 | .1671 | 1.170 | 0.021 |  | 1031
[23 empty] | Larkspur | 61 | .1302 | 1.172 | 0.021 |  | 1032
[23 empty] | Marigold | 61 | .1351 | 1.216 | 0.0195 |  | 1079
[23 empty] | Hawthorn | 61 | .1398 | 1.258 | 0.0183 |  | 1124
[23 empty] | Narcissus | 61 | .1444 | 1,300 | 0.0173 |  | 1169
[23 empty] | Columbine | 61 | .1489 | 1.340 | 0.0163 |  | 1212
[23 empty] | Carnation | 61 | .1532 | 1.379 | 0.0155 |  | 1253
[23 empty] | Gladiolus | 61 | .1574 | 1.417 | 0.0147 |  | 1294
[23 empty] | Coreopsis | 61 | .1614 | 1.454 | 0.0141 |  | 1333
[23 empty] | Jessamine | 61 | .1694 | 1.525 | 0.0129 |  | 1408
[23 empty] | Cowslip | 91 | .1482 | 1.630 | 0.0115 |  | 1518
[23 empty] | Sagebrush | 91 | .1572 | 1.729 | 0.0105 |  | 1612
[23 empty] | Lupine | 91 | .1657 | 1.823 | 0.00969 |  | 1706
[23 empty] | Bitterroot | 91 | .1739 | 1.913 | 0.009 |  | 1793
[23 empty] | Trilium | 127 | .1537 | 1.996 | 0.00384 |  | 1874
[23 empty] | Bluebonnet | 127 | .1660 | 2.158 | 0.00756 |  | 2024
Main Sheet