## Conduit Size
Jignesh.Parmar
www.electricalnotes.wordpress.com
jiguparmar@yahoo.com
No of Conductor | Size of Conductor | Type of Insulation | Calculated Area |  |  | Type of Insulation
1 | 2AWG(35 mm2) | THHN | 0.1158 |  |  | RHW | = RHW & RHW
2 | 12AWG(4 mm2) | RHW | 0.0706 |  |  | THHN | = THHN & THWN
5 | 1/0AWG(55 mm2) | RHW | 1.5195 |  |  | THW | = THW, TW, & THWN
1 | 10AWG(6 mm2) | RHW | 0.0437 |  |  | XHHW | = XHHW & XHH
[6 empty] | LV | Low Voltage Cable
[6 empty] | Fiber | Fiber Optic Cable
Type of Conduit
No of Conductor | Type of Cable | Size of Conductor | Calculated Area |  |  | EMT | = Electrical Metallic Tubing (Thinwall)
[6 empty] | ENT | = Electrical Non-Metallic Tubing (Smurf Tube)
1 | Fiber | 2f | 0.02659 |  |  | FMC | = Flexible Metal Conduit
1 | LV | CAT5 | 0.034636 |  |  | IMC | = Intermediate Metal Conduit
[6 empty] | LFNC_A | = Liquidtight Flexible Non-Metallic Conduit Type A
[6 empty] | LFNC_B | = Liquidtight Flexible Non-Metallic Conduit Type B
[6 empty] | LFMC | = Liquidtight Flexible Metal Conduit (Sealtite)
[6 empty] | RMC | = Rigid Metal Conduit (GRC)
[6 empty] | PVC-40 | = Schedule 40 PVC (Plastic)
[6 empty] | PVC-80 | = Schedule 80 PVC (Plastic)
| Total Area |  | 1.8108 | 1.8108 | 0.4
| Conduit Type |  | RMC | 4.5271
| Minimum Conduit Size |  | 2-1/2"
DESIGN OF CONDUIT SIZE FOR LT/CAT-5/FIBRE OPTICAL CABLE

## Sheet2
Wire Size | THW Size | THHN Size | RHW Size | XHHW Size | Conduit Table | Conduit Fill Rates |  |  | Cable Table | Low Voltage Wire Size |  | Fiber Wire Size
14 AWG(2.5 mm2) | 0.0139 | 0.0097 | 0.0293 | 0.0139 | EMT |  |  |  | LV
12AWG(4 mm2) | 0.0181 | 0.0133 | 0.0353 | 0.0181 | ENT | 1 | 53% |  | Fiber | 22/2 | 0.014741 | 2f | 0.02659
10AWG(6 mm2) | 0.0243 | 0.0211 | 0.0437 | 0.0243 | FMC | 2 | 31% |  |  | 22/3 | 0.017203 | 4f | 0.031416
8AWG(10 mm2) | 0.0437 | 0.0366 | 0.0835 | 0.0437 | IMC | 3 | 40% |  |  | 22/4 | 0.020106 | 6f | 0.038013
6AWG(16 mm2) | 0.0726 | 0.0507 | 0.1041 | 0.059 | LFNC_A |  |  |  |  | 22/6 | 0.028353 | 8f | 0.043374
4AWG(25 mm2) | 0.0973 | 0.0824 | 0.1333 | 0.0814 | LFNC_B |  |  |  |  | 22/8 | 0.034636 | 12f | 0.051071
3AWG(35 mm2) | 0.1134 | 0.0973 | 0.1521 | 0.0962 | LFMC |  |  |  |  | 20/2 | 0.018385 | 24f | 0.19322
2AWG(35 mm2) | 0.1333 | 0.1158 | 0.175 | 0.1146 | RMC |  |  |  |  | 20/3 | 0.021382 | 36f | 0.32573
1AWG(50 mm2) | 0.1901 | 0.1562 | 0.266 | 0.1534 | PVC40 |  |  |  |  | 20/4 | 0.025447 | 48f | 0.30876
1/0AWG(55 mm2) | 0.2223 | 0.1855 | 0.3039 | 0.1825 | PVC80 |  |  |  |  | 20/6 | 0.035299 | 72f | 0.48275
2/0AWG(70 mm2) | 0.2624 | 0.2223 | 0.3505 | 0.219 | [5 empty] | 18/2 | 0.022167 | 96f | 0.72533
3/0AWG(95 mm2) | 0.3117 | 0.2679 | 0.4072 | 0.2642 | Type of Insulation |  |  |  |  | 18/3 | 0.02688 | 144f | 0.84459
4/0AWG(120 mm2) | 0.3718 | 0.3237 | 0.4754 | 0.3197 | RHW | = RHW & RHW |  |  |  | 18/4 | 0.031731
250 Kcmill | 0.4596 | 0.397 | 0.6291 | 0.3904 | THHN | = THHN & THWN |  |  |  | 18/6 | 0.049087
300 Kcmill | 0.5281 | 0.4608 | 0.7088 | 0.4536 | THW | = THW, TW, & THWN |  |  |  | 18/8 | 0.066052
350 Kcmill | 0.5958 | 0.5242 | 0.787 | 0.5166 | XHHW | = XHHW & XHH |  |  |  | 16/2 | 0.028652
400 Kcmill | 0.6619 | 0.5863 | 0.8626 | 0.5782 | [5 empty] | 16/4 | 0.044863
500 Kcmill | 0.7901 | 0.7073 | 1.0082 | 0.6984 | [5 empty] | 14/2 | 0.047916
600 Kcmill | 0.9729 | 0.8676 | 1.2135 | 0.8709 | [5 empty] | 14/4 | 0.069279
700 Kcmill | 1.101 | 0.9887 | 1.3561 | 0.9923 | [5 empty] | 12/2 | 0.066052
750 Kcmill | 1.1652 | 1.0496 | 1.4272 | 1.0532 | [5 empty] | 12/4 | 0.088141
800 Kcmill | 1.2272 | 1.1085 | 1.4957 | 1.1122 | [5 empty] | CAT3 | 0.034636
900 Kcmill | 1.3561 | 1.2311 | 1.6377 | 1.2351 | [5 empty] | CAT5 | 0.034636
1000 Kcmill | 1.4784 | 1.3478 | 1.7719 | 1.3519
EMT Conduit | Dia |  | RMC Conduit | Dia | PVC-80 Conduit | Dia |  | ENT Conduit | Dia | FMC Conduit | Dia | IMC Conduit | Dia | LFNC-A Conduit | Dia | LFNC-B Conduit | Dia | LFMC Conduit |  | PVC-40 Conduit
0 | 1/2" |  | 0 | 1/2" | 0 | 1/2" |  | 0 | 1/2" | 0 | 3/8" | 0 | 1/2" | 0 | 3/8" | 0 | 3/8" | 0 | 3/8" | 0 | 1/2"
0.304 | 1/2" |  | 0.314 | 1/2" | 0.217 | 1/2" |  | 0.246 | 1/2" | 0.116 | 3/8" | 0.342 | 1/2" | 0.192 | 3/8" | 0.192 | 3/8" | 0.192 | 3/8" | 0.258 | 1/2"
0.305 | 3/4" |  | 0.315 | 3/4" | 0.218 | 3/4" |  | 0.247 | 3/4" | 0.117 | 1/2" | 0.343 | 3/4" | 0.193 | 1/2" | 0.193 | 1/2" | 0.193 | 1/2" | 0.259 | 3/4"
0.533 | 3/4" |  | 0.549 | 3/4" | 0.409 | 3/4" |  | 0.454 | 3/4" | 0.317 | 1/2" | 0.586 | 3/4" | 0.312 | 1/2" | 0.314 | 1/2" | 0.314 | 1/2" | 0.508 | 3/4"
0.534 | 1" |  | 0.55 | 1" | 0.41 | 1" |  | 0.455 | 1" | 0.318 | 3/4" | 0.587 | 1" | 0.313 | 3/4" | 0.315 | 3/4" | 0.315 | 3/4" | 0.509 | 1"
0.864 | 1" |  | 0.887 | 1" | 0.688 | 1" |  | 0.785 | 1" | 0.533 | 3/4" | 0.959 | 1" | 0.535 | 3/4" | 0.541 | 3/4" | 0.541 | 3/4" | 0.832 | 1"
0.865 | 1-1/4" |  | 0.888 | 1-1/4" | 0.689 | 1-1/4" |  | 0.786 | 1-1/4" | 0.534 | 1" | 0.96 | 1-1/4" | 0.536 | 1" | 0.542 | 1" | 0.542 | 1" | 0.833 | 1-1/4"
1.496 | 1-1/4" |  | 1.526 | 1-1/4" | 1.237 | 1-1/4" |  | 1.41 | 1-1/4" | 0.817 | 1" | 1.647 | 1-1/4" | 0.854 | 1" | 0.873 | 1" | 0.873 | 1" | 1.453 | 1-1/4"
1.497 | 1-1/2" |  | 1.527 | 1-1/2" | 1.238 | 1-1/2" |  | 1.411 | 1-1/2" | 0.818 | 1-1/4" | 1.648 | 1-1/2" | 0.855 | 1-1/4" | 0.874 | 1-1/4" | 0.874 | 1-1/4" | 1.454 | 1-1/2"
2.036 | 1-1/2" |  | 2.071 | 1-1/2" | 1.711 | 1-1/2" |  | 1.936 | 1-1/2" | 1.277 | 1-1/4" | 2.225 | 1-1/2" | 1.502 | 1-1/4" | 1.528 | 1-1/4" | 1.528 | 1-1/4" | 1.986 | 1-1/2"
2.037 | 2" |  | 2.072 | 2" | 1.712 | 2" |  | 1.937 | 2" | 1.278 | 1-1/2" | 2.226 | 2" | 1.503 | 1-1/2" | 1.529 | 1-1/2" | 1.529 | 1-1/2" | 1.987 | 2"
3.356 | 2" |  | 3.408 | 2" | 2.874 | 2" |  | 3.205 | 2" | 1.858 | 1-1/2" | 3.63 | 2" | 2.018 | 1-1/2" | 1.981 | 1-1/2" | 1.981 | 1-1/2" | 3.291 | 2"
3.357 | 2-1/2" |  | 3.409 | 2-1/2" | 2.875 | 2-1/2" |  | 3.206 | N/A | 1.859 | 2" | 3.631 | 2-1/2" | 2.019 | 2" | 1.982 | 2" | 1.982 | 2" | 3.292 | 2-1/2"
5.858 | 2-1/2" |  | 4.866 | 2-1/2" | 4.119 | 2-1/2" |  |  |  | 3.269 | 2" | 5.135 | 2-1/2" | 3.343 | 2" | 3.246 | 2" | 3.246 | 2" | 4.695 | 2-1/2"
5.859 | 3" |  | 4.867 | 3" | 4.12 | 3" |  |  |  | 3.27 | 2-1/2" | 5.136 | 3" | 3.344 | N/A | 3.247 | N/A | 3.247 | 2-1/2" | 4.696 | 3"
8.846 | 3" |  | 7.499 | 3" | 6.442 | 3" |  |  |  | 4.909 | 2-1/2" | 7.922 | 3" |  |  |  |  | 4.881 | 2-1/2" | 7.268 | 3"
8.847 | 3-1/2" |  | 7.5 | 3-1/2" | 6.443 | 3-1/2" |  |  |  | 4.91 | 3" | 7.923 | 3-1/2" |  |  |  |  | 4.882 | 3" | 7.269 | 3-1/2"
11.545 | 3-1/2" |  | 10.01 | 3-1/2" | 8.688 | 3-1/2" |  |  |  | 7.069 | 3" | 10.584 | 3-1/2" |  |  |  |  | 7.475 | 3" | 9.737 | 3-1/2"
11.546 | 4" |  | 10.011 | 4" | 8.689 | 4" |  |  |  | 7.07 | 3-1/2" | 10.585 | 4" |  |  |  |  | 7.476 | 3-1/2" | 9.738 | 4"
14.753 | 4" |  | 12.882 | 4" | 11.258 | 4" |  |  |  | 9.621 | 3-1/2" | 13.631 | 4" |  |  |  |  | 9.731 | 3-1/2" | 12.554 | 4"
14.754 | N/A |  | 12.883 | 5" | 11.259 | 5" |  |  |  | 9.622 | 4" | 13.632 | N/A |  |  |  |  | 9.732 | 4" | 12.555 | 5"
|  |  | 20.212 | 5" | 17.855 | 5" |  |  |  | 12.566 | 4" | [6 empty] | 12.692 | 4" | 19.761 | 5"
|  |  | 20.213 | 6" | 17.856 | 6" |  |  |  | 12.567 | N/A | [6 empty] | 12.693 | N/A | 19.762 | 6"
|  |  | 29.158 | 6" | 25.598 | 6" | [13 empty] | 28.567 | 6"
|  |  | 29.159 | N/A | 25.599 | N/A | [13 empty] | 28.568 | N/A
Cable Size Table
22/2
22/3
22/4
22/6
22/8
20/2
20/3
20/4
20/6
18/2
18/3
18/4
18/6
18/8
16/2
16/4
14/2
14/4
12/2
12/4
CAT3
CAT5
2f
4f
6f
8f
12f
24f
36f
48f
72f
96f
144f