## Motor Calculator
IEC Motor Data Calculator
BASED ON THE 2011 NEC
|  | Three Phase |  |  | Single Phase
Horse Power
[5 empty] | 115V | 230V
[5 empty] | 16 | 8 | Full Load Amps (FLA)
| 15.2 | Full Load Amps (FLA) |  |  | 14 | 14 | Wire Size
| 14 | Wire Size |  |  | 25 | 12 | Time-Delay Fuse Rating (Amps)
| 25 | Time-Delay Fuse Rating (Amps) |  |  | 25 | 15 | PowerPact Breaker Size (Amps)
| 30 | PowerPact MCP Size (Amps) |  | LC1 | D12 | D09 | IEC Contactor Cat #
LC1 | D18 | IEC Contactor Cat # |  | LRD | 21 | 14 | IEC Overload Relay Cat #
LR | D21 | IEC Overload Relay Cat #
TeSys U Self-Protected Starters Selection Table
Scheduler
Enter Start Date (M/D/YY)
2011-01-01
7.6 |  | Full Load Amps (FLA)
LUB12 |  | TeSys U Power Base | [5 empty] | Enter Number of Weeks
LUCA12 |  | TeSys U Control Unit | [5 empty] | 10
End Date
| Click here for Wire & Cable | [6 empty] | 2011-03-12
Voltage
Horse Power
Horse Power
Voltage

## Data (hidden)
| 200V | [22 empty] | HP |  | Voltage |  | Phase
| Horse Power | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 75 | 100 | 125 | 150 | 200 | 1 | 0.5 hp | 1 | 200 (208) | 200 | 1-Phase | 2
A | FLA | 2.5 | 3.7 | 4.8 | 6.9 | 7.8 | 11 | 17.5 | 25.3 | 32.2 | 48.3 | 62.1 | 78.2 | 92 | 120 | 150 | 177 | 221 | 285 | 359 | 414 | 552 | 2 | 0.75 hp | 2 | 230 (240) | 230 | 3-Phase
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1/0 | 3/0 | 4/0 | 300 | 500 | 2-4/0 | 2-300 | 3-300 | 3 | 1 hp | 3 | 460 (480) | 460
C | Time Delay Fuse Rating | 4 | 6.25 | 8 | 10 | 12 | 17.5 | 25 | 40 | 50 | 60 | 90 | 100 | 125 | 175 | 200 | 250 | 300 | 400 | 500 | 600 | - | 4 | 1.5 hp | 4 | 575 (600) | 575
D | PowerPact MCP Size | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 100 | 100 | 100 | 150 | 150 | 250 | 250 | - | - | - | - | - | 5 | 2 hp |  | Voltage |  | 230 | 2
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D09 | D12 | D18 | D25 | D32 | D50A | D65A | D80 | D115 | D150 | F185 | F265 | F330 | F400 | F500 | F500 | F630 | 6 | 3 hp |  | HP |  | 5 hp | 7
F | Overload Relay # LR | D07 | D08 | D10 | D12 | D12 | D16 | D21 | D32 | D35 | D350 | D365 | D3363 | D4365 | D4369 | 9F5369 | 9F5371 | 9F7375 | 9F7375 | 9F7379 | 9R7379 | 9F7381 | 7 | 5 hp | A | FLA |  |  | 15.2
G | [22 empty] | 8 | 7.5 hp | B | Wire Size |  |  | 14
H | [22 empty] | 9 | 10 hp | C | Time Delay Fuse Rating |  |  | 25
I | [22 empty] | 10 | 15 hp | D | PowerPact Circuit Breaker Size |  |  | 30
| 230 | [21 empty] | 11 | 20 hp | E | IEC Contact Catalog Number |  |  | D18
A | FLA | 2.2 | 3.2 | 4.2 | 6.0 | 6.8 | 9.6 | 15.2 | 22 | 28 | 42 | 54 | 68 | 80 | 104 | 130 | 154 | 192 | 248 | 312 | 360 | 480 | 12 | 25 hp | F | IEC Relay Catalog Number |  |  | D21
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 10 | 6 | 4 | 4 | 3 | 1 | 2/0 | 3/0 | 250 | 350 | 2-3/0 | 2-4/0 | 2-350 | 13 | 30 hp
C | Time Delay Fuse Rating | 4 | 5.6 | 8 | 10 | 10 | 15 | 25 | 30 | 40 | 60 | 90 | 100 | 100 | 150 | 200 | 200 | 300 | 350 | 400 | 500 | 600 | 14 | 40 hp
D | PowerPact MCP Size | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 100 | 100 | 100 | 150 | 150 | 250 | 250 | - | - | - | - | 15 | 50 hp
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D09 | D12 | D18 | D25 | D32 | D50A | D65A | D80 | D80 | D115 | D150 | F185 | F265 | F330 | F400 | F500 | F500 | 16 | 60 hp
F | Overload Relay # LR | D07 | D08 | D10 | D12 | D12 | D14 | D21 | D22 | D32 | D350 | D365 | D3361 | D3363 | D4367 | D4369 | 9F5371 | 9F5371 | 9F7375 | 9F7375 | 9F7379 | 9F7379 | 17 | 75 hp
G | [22 empty] | 18 | 100 hp
H | [22 empty] | 19 | 125 hp
I | [22 empty] | 20 | 150 hp
| 460 | [21 empty] | 21 | 200 hp
A | FLA | 1.1 | 1.6 | 2.1 | 3.0 | 3.4 | 4.8 | 7.6 | 11 | 14 | 21 | 27 | 34 | 40 | 52 | 65 | 77 | 96 | 124 | 156 | 180 | 240
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 10 | 8 | 8 | 6 | 4 | 3 | 1 | 2/0 | 3/0 | 4/0 | 250
C | Time Delay Fuse Rating | 2 | 3.2 | 4 | 5.6 | 5.6 | 8 | 12 | 17.5 | 20 | 30 | 40 | 50 | 60 | 80 | 100 | 100 | 150 | 175 | 200 | 250 | 350
D | PowerPact MCP Size | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 100 | 100 | 100 | 150 | 150 | 250 | 250 | -
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D09 | D09 | D09 | D12 | D18 | D25 | D32 | D40A | D40A | D50A | D80 | D80 | D115 | D150 | F185 | F265 | F330
F | Overload Relay # LR | D06 | D07 | D07 | D08 | D08 | D10 | D12 | D16 | D21 | D22 | D32 | D340 | D350 | D365 | D3361 | D3363 | D4365 | D4369 | 9F5371 | 9F5371 | 9F7375
G
H
I
575
A | FLA | 0.9 | 1.3 | 1.7 | 2.4 | 2.7 | 3.9 | 6.1 | 9 | 11 | 17 | 22 | 27 | 32 | 41 | 52 | 62 | 77 | 99 | 125 | 144 | 192
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 10 | 8 | 6 | 6 | 4 | 3 | 1 | 2/0 | 3/0 | 250
C | Time Delay Fuse Rating | 1.8 | 2.5 | 3.2 | 4 | 4.5 | 6.25 | 10 | 15 | 17.5 | 25 | 30 | 40 | 50 | 60 | 80 | 90 | 100 | 150 | 175 | 200 | 300
D | PowerPact MCP Size | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 100 | 100 | 100 | 150 | 150 | 250 | 250
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D09 | D09 | D09 | D09 | D12 | D18 | D25 | D32 | D32 | D50A | D65A | D80 | F115 | F115 | F150 | F185 | F330
F | Overload Relay # LR | D05 | D06 | D07 | D07 | D08 | D08 | D12 | D14 | D16 | D21 | D22 | D32 | D35 | D350 | D365 | D3361 | 9F5367 | 9F5369 | 9F5369 | 9F5369 | 9F5371
G
H
I
| Single Phase 115V | [22 empty] | HP | Single Phase |  | 6
| HP | 1/6 | 1/4 | 1/3 | 1/2 | 3/4 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | [10 empty] | 1 | 1/6 hp |  | HP |  | 0.75 hp | 120V | 240V
| Voltage | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | [10 empty] | 2 | 1/4 hp |  | Voltage |  | 575
A | FLA | 4.4 | 5.8 | 7.2 | 9.8 | 13.8 | 16 | 20 | 24 | 34 | 56 | 80 | [10 empty] | 3 | 1/3 hp |  | FLA | A |  | 16 | 8
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | 4 | 3 | [10 empty] | 4 | 1/2 hp |  | Wire Size | B |  | 14 | 14
C | Time Delay Fuse Rating | 7 | 9 | 12 | 15 | 20 | 25 | 30 | 30 | 50 | 80 | 100 | [10 empty] | 5 | 3/4hp |  | Time Delay Fuse Rating | C |  | 25 | 12
D | PowerPact Breaker Size | 15 | 15 | 15 | 15 | 20 | 25 | 30 | 40 | 50 | 80 | 100 | [10 empty] | 6 | 1 hp |  | MAG-GARD Circuit Breaker Size | D |  | 25 | 15
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D12 | D12 | D25 | D25 | D40A | D65A | D80 | [10 empty] | 7 | 1.5hp |  | IEC Contactor Catalog Number | E |  | D12 | D09
F | Overload Relay # LRD | 10 | 12 | 14 | 16 | 21 | 21 | 22 | 32 | 340 | 365 | 3363 | [10 empty] | 8 | 2 hp |  | IEC Overload Relay Catalog Number | F |  | 21 | 14
[23 empty] | 9 | 3 hp
| Single Phase 230V | [21 empty] | 10 | 5 hp
| HP | 1/6 | 1/4 | 1/3 | 1/2 | 3/4 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | [10 empty] | 11 | 7.5 hp |  | Voltage
| Voltage | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | [12 empty] | 1 | 200 (208) | 200
A | FLA | 2.2 | 2.9 | 3.6 | 4.9 | 6.9 | 8 | 10 | 12 | 17 | 28 | 40 | [12 empty] | 2 | 230 (240) | 230
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | [12 empty] | 3 | 460 (480) | 460
C | Time Delay Fuse Rating | 3.5 | 4.5 | 5.6 | 8 | 10 | 12 | 15 | 17.5 | 25 | 40 | 60 | [12 empty] | 4 | 575 (600) | 575
D | PowerPact Breaker Size | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 25 | 40 | 60
E | Contactor Cat # LC1 | D09 | D09 | D09 | D09 | D09 | D09 | D12 | D12 | D18 | D32 | D50A
F | Overload Relay # LRD | 07 | 08 | 08 | 10 | 12 | 14 | 16 | 16 | 21 | 32 | 350
Starter selector
| HP | 0.5 | 0.75 | 1 | 1.5 | 2.0 | 3.0 | 5 | 7.5 | 10 | 15 | 20 | 25 | [9 empty] | 1 | 0.5 hp |  | Voltage
| Voltage | 208V | 208V | 208V | 208V | 208V | 208V | 208V | 208V | 208V | 208V | 208V | 208V | [9 empty] | 2 | 0.75 hp | 1 | 200 (208) | 208
A | FLA | 2.5 | 3.7 | 4.8 | 6.9 | 7.8 | 11 | 17.5 | 25.3 | 32.2 | 48.3 | 62.1 | 78.2 | [9 empty] | 3 | 1 hp | 2 | 230 (240) | 240 |  | 6
B | Power Base | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB32 | LUB32 | LUB32 | N/A | N/A | N/A | [9 empty] | 4 | 1.5 hp | 3 | 460 (480) | 480
C | Control Unit | LUCA05 | LUCA05 | LUCA05 | LUCA12 | LUCA12 | LUCA12 | LUCA18 | LUCA32 | LUCA32 | N/A | N/A | N/A | [9 empty] | 5 | 2 hp | 4 | 575 (600) | 600
| Voltage | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | 240V | [9 empty] | 6 | 3 hp |  | Voltage |  | 480 | 3
A | FLA | 2.5 | 3.2 | 4.2 | 6 | 6.8 | 9.6 | 15.2 | 22 | 28 | 42 | 54 | 68 | [9 empty] | 7 | 5 hp |  | HP |  | 5 hp | 7
B | Power Base | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB32 | LUB32 | LUB32 | N/A | N/A | N/A | [9 empty] | 8 | 7.5 hp |  | FLA | A |  | 7.6
C | Control Unit | LUCA05 | LUCA05 | LUCA05 | LUCA12 | LUCA12 | LUCA12 | LUCA18 | LUCA32 | LUCA32 | N/A | N/A | N/A | [9 empty] | 9 | 10 hp |  | IEC Contactor Catalog Number | B |  | LUB12
| Voltage | 480V | 480V | 480V | 480V | 480V | 480V | 480V | 480V | 480V | 480V | 480V | 480V | [9 empty] | 10 | 15 hp |  | IEC Overload Relay Catalog Number | C |  | LUCA12
A | FLA | 1.1 | 1.6 | 2.1 | 3 | 3.4 | 4.8 | 7.6 | 11 | 14 | 21 | 27 | 34 | [9 empty] | 11 | 20 hp
B | Power Base | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB32 | LUB32 | LUB32 | N/A | [9 empty] | 12 | 25 hp
C | Control Unit | LUCA1X | LUCA05 | LUCA05 | LUCA05 | LUCA05 | LUCA05 | LUCA12 | LUCA12 | LUCA18 | LUCA32 | LUCA32 | N/A
| Voltage | 600V | 600V | 600V | 600V | 600V | 600V | 600V | 600V | 600V | 600V | 600V | 600V
A | FLA | 0.9 | 1.3 | 1.7 | 2.4 | 2.7 | 3.9 | 6.1 | 9 | 11 | 17 | 22 | 27
B | Power Base | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB12 | LUB32 | LUB32 | LUB32
C | Control Unit | LUCA1X | LUCA1X | LUCA05 | LUCA05 | LUCA05 | LUCA05 | LUCA12 | LUCA12 | LUCA12 | LUCA18 | LUCA32 | LUCA32

## Wire & Conduit
Wire and Conduit Data
BASED ON THE 2011 NEC
Select Wire Size AWG/kcmil
Based on Appendix C - Tables
|  | C1 and C1A |  |  |  |  | Select Wire Size
COPPER |  |  |  | Ampacity at 75C based on NEC Table 310.15 | 85
| THW, THW-2 THHW |  |  | 3 WIRES - INCHES | 1
|  |  |  | 3 Phase 4 Wire - INCHES | 11/4
| THHN, THWN, XHHW, |  |  | 3 WIRES - INCHES | 1
| THWN-2, XHHW-2 |  |  | 3 Phase 4 Wire - INCHES | 1
ALUMINUM |  |  |  | Ampacity at 75C based on NEC Table 310.15 | 65
| THW, THW-2 THHW |  |  | 3 WIRES - INCHES | 1
|  |  |  | 3 Phase 4 Wire - INCHES | 1
| THHN, THWN, XHHW, |  |  | 3 WIRES - INCHES | 3/4
| THWN-2, XHHW-2 |  |  | 3 Phase 4 Wire - INCHES | 1
Notes:
Ampacity of conductors based on 30 C ambient.
|  |  |  | Voltage Drop Calculator |  |  | Conduit sizes for aluminum based on the
use of compact conductors
|  |  | Select Wire Size at Top | 4 |  |  | Where a major portion of the load consists of nonlinear loads,
|  |  | Enter Distance in Multiples of 100 ft (i.e. 100ft=1) | 12 |  | Enter Distance | the neutral is considered to be current carrying.
|  |  | Enter Amperage | 15 |  | Enter Amperage | On 4-wire applications, derate the ampacity to 80% per
| Line to Line Volts Drop | 1 Phase Volts | 95% PF | 10.98 |  |  | note 8 and note 10© of the NEC ampacity tables.
| Per Ampere per 100ft. In |  | 80% PF | 9.9
| Magnetic Conduit Copper Wire | 3 Phase Volts | 95% PF | 9.54
|  |  | 80% PF | 8.64

## Wire Data (hidden)
0 | 100
6
#14 | A | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
#12 | B | 20 | 25 | 35 | 50 | 65 | 85 | 100 | 115 | 130 | 150 | 175 | 200 | 230 | 255 | 285 | 310 | 335 | 380 | 420 | 460 | 475 | 490 | 520 | 545
#10 | C | 1/2 | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | 3 | 3 1/2 | 3 1/2
#8 | D | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 11/4 | 1 1/4 | 1 1/4 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | 3 1/2 | 4 | 4 | 4
#6 | E | 1/2 | 1/2 | 1/2 | 1/2 | 3/4 | 1 | 1 | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | 3 | 3 | 3 1/2
#4 | F | 1/2 | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 1 1/4 | 1 1/4 | 1 1/4 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | 3 1/2 | 4 | 4
#3 | G | N/A | N/A | N/A | 40 | 50 | 65 | 75 | 90 | 100 | 120 | 135 | 155 | 180 | 205 | 230 | 250 | 270 | 310 | 340 | 375 | 385 | N/A | N/A | 445
#2 | H | N/A | N/A | N/A | 3/4 | 3/4 | 1 | N/A | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | N/A | N/A | 3 1/2
#1 | I | N/A | N/A | N/A | 3/4 | 1 | 1 | N/A | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | N/A | N/A | 4
1/0 | J | N/A | N/A | N/A | 1/2 | 3/4 | 3/4 | N/A | 1 | 1 1/4 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | N/A | N/A | 3
2/0 | K | N/A | N/A | N/A | 3/4 | 3/4 | 1 | N/A | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | N/A | N/A | 4
3/0 | L | 0.58 | 0.37 | 0.23 | 0.15 | 0.095 | 0.061 | 0.048 | 0.04 | 0.032 | 0.027 | 0.022 | 0.017 | 0.015 | 0.013 | 0.012 | 0.010 | 0.0094 | 0.0082 | 0.0074 | 0.0068 | 0.0066 | - | - | -
4/0 | M | 0.5 | 0.31 | 0.20 | 0.13 | 0.084 | 0.055 | 0.045 | 0.037 | 0.03 | 0.027 | 0.022 | 0.018 | 0.016 | 0.014 | 0.013 | 0.012 | 0.011 | 0.0098 | 0.0092 | 0.0085 | 0.0084 | - | - | -
250 | N | 0.5 | 0.32 | 0.20 | 0.13 | 0.082 | 0.053 | 0.042 | 0.035 | 0.028 | 0.023 | 0.019 | 0.015 | 0.013 | 0.011 | 0.01 | .0088 | 0.0081 | 0.0071 | 0.0064 | 0.0059 | 0.0057 | - | - | -
300 | O | 0.43 | 0.27 | 0.17 | 0.11 | 0.073 | 0.048 | 0.039 | 0.032 | 0.026 | 0.023 | 0.019 | 0.016 | 0.014 | 0.012 | 0.011 | 0.010 | 0.0095 | 0.0085 | 0.0080 | 0.0074 | 0.0073 | - | - | -
350
400 | #8 XHHW and XHHW-2 CU requires 3/4" conduit for 3 wires
500 | #6 XHHW and XHHW-2 CU Requires 1" conduit for 4 wires
600 | 750 kcmil AL SHHW and XHHW-2 requires 3 1/2 conduit for 4 Wires
700
750
800
900
1000

## Instructions and Notes
Instructions
Motor Calculator
Three Phase and Single Phase
Click on the Voltage and HP to view information for your application
Scheduler
Enter the Start Date (MM/DD/YYYY format) and the number of weeks to view the resulting End Date. Helpful in determining ship dates and project schedules.
Wire and Conduit Page
Use the dropdown list to select wire size to view information.
Voltage Drop
Select wire size as before.
Enter the cable run distance in multiples of 100 ft. (i.e.. 100ft - 1)
Enter the amperage you will be drawing through the wire.
View the voltage drop based on PF.
For other tools, please visit | www.Schneider-Electric.us
Notes: Fuses and circuit breakers shown are for short-circuit ground fault protection only. This data applies to Normal Service applications of switches, starters or breakers shown. Do not use for Heavy Service applications, as defined in the latest Catalog Digest. Data is based on information available at time of publication and is subject to change. See actual installed equipment and Section 110-14C for termination requirements. Fuse sizes and circuit breaker trip amperes are approximate selections suitable for most installations. Thermal unit selectors are not based on NEC currents (see NEC 430-6) but are selected from average full load currents. Thermal units can be more accurately selected using table furnished with starter and full load current marked on the motor name plate.