## Capacitor
jignesh.Parmar, www.electricalnotes.wordpress.com jiguparmar@yahoo.com
POWER FACTOR CORRECTION |  |  |  |  | RESULT
| Supply System | 3 |  |  |  | Leading KVAR | 282.2217 | Kvar | Tanф1 | 0.75 |  | 0.6 | 0.75 | Kw
[12 empty] | 0.199 | 0.20306 | HP
| Supplay Voltage | 415 |  |  |  | Leading KVAR supplied by each Phase | 94.0739 | Kvar/Phase | Tanф2 | 0.20306 |  |  |  | Kva
Star
| Supplay Frequency | 50 |  |  |  | Capacitance of Capacitor | 5203.737 | μF | Kvar | 282.2217 |  |  |  | Delta
| Input Power | 516 | Kw |  |  | Required Capacitor is | 3 No of | 282.22 Kvar | Kavar/Phase | 94.0739 |  |  |  | 1
|  | 516 | 645 | [10 empty] | 3
| Efficiency | 100 | % | 1 |  | Leading Kvar/Phase is | 94.0739 | Kvar/Phase | 2*TT*f*V | 75361.9047
| Amp | 897.3538 | Amp |  |  | Before P.F Correction |  |  | Kvar/Phase | =v*IC*1000
| Old Power Factor (Cosф1) | 0.8 |  |  |  | Max Demand | 645 | Kva | IC | 392.1635
[9 empty] | IC | =2*TT*f*V*C
| Desire Power Factor(Cosф2) | 0.98 |  |  |  | KVA Demand Charge | 64500 | R.S | C | 5203.737
| Capacitor Connected in | Star |  |  |  | Unit Consumed/Year | 4520160 | Kwh
Before
| Daily Working Hours | 24 | Hr. |  |  | Energy Charge/Year | 45201600 | R.S | Max Demand | 645 | Kva
[9 empty] | KVA Demand Charge | 64500 | R.S
| Tarrif Charge/Kva | 100 | R.S |  |  | Total Annual Cost | 45266100 | R.S | Unit Consumed/Year | 4520160 | Kwh
[9 empty] | Energy Charge/Year | 45201600 | R.S
| Tarrif Charge/Kw | 10 | R.S |  |  | After P.F Correction |  |  | Total Annual Cost | 45266100 | R.S
| Capacitor Cost/Kva | 60 | R.S |  |  | Max Demand | 526.5306 | Kva | After
[9 empty] | Max Demand | 526.5306 | Kva
| Annual Intrest & Depriciation/Capacitor | 12 | % |  |  | KVA Demand Charge | 52653.0612 | R.S | KVA Demand Charge | 52653.0612 | R.S
[9 empty] | Unit Consumed/Year | 4520160 | Kwh
[6 empty] | Unit Consumed/Year | 4520160 | Kwh | Energy Charge/Year | 45201600 | R.S
[9 empty] | Total Annual Cost | 45254253.0612 | R.S
[6 empty] | Energy Charge/Year | 45201600 | R.S
[9 empty] | Capital Cost of capacitor | 16933.3 | R.S
[6 empty] | Total Annual Cost | 45254253.0612 | R.S | Annual Inte and Dep | 2032 | R.S
[9 empty] | Total Annual Cost | 45256285.06 | R.S
[6 empty] | Capital Cost of capacitor | 16933.3 | R.S | Annual Saving | 9814.94
[6 empty] | Annual Inte and Dep | 2032 | R.S
[6 empty] | Annual Cost before P.F Correction: | 45266100 | R.S
[6 empty] | Annual Cost After P.F Correction: | 45256285.06 | R.S
[6 empty] | Annual Saving | 9814.94 | R.S
size of capacitor for power factor correction