## Branch Circuit
| Jignesh.Parmar www.electricalnotes.wordpress.com jiguparmar@yahoo.com | [5 empty] | SELECTION OF MAIN CIRCUIT C.B AND BRANCH CIRCUIT C.B , WIRE
[12 empty] | RCCB |  |  | MCCB Rating(min)As per NEC 210.
[12 empty] | Size(Amp) | 63
[12 empty] | Type | D Type |  | Roughly Estimate of ISC(KA) At this Point
[12 empty] | Triping(Amp) | 725.0686 |  | Near 3 Ph T.C Kva |  |  | 1000
N.B : Enter Your Detail in white Background Cells | [5 empty] | 2. ENTER LOAD DATA | [5 empty] | Sen.I∆n | I∆n:30ma |  | Rough ISC(KA) |  |  | 27.86
[12 empty] | Brea.Cap(KA). | min 28 |  | OR Known Value of ISC(KA)
[6 empty] | 3. SELECT BRANCH C.B | [5 empty] | Pole | 3or4 |  | Final ISC(KA) |  |  | 28
[12 empty] | Load (Amp) | 36.2534
As Per NEC section:210
[45 empty] | 1 | Ltg | B | Cont | 23.5786 |  | AWG
RCB |  |  | MCCB |  |  | MCB |  |  | MCCB |  |  | RCCB |  | 4 | RCCB |  |  | RCCB |  |  | ELCB |  |  | RCB |  |  | RCCB |  |  | RCBO |  |  | ELCB |  |  | RCB |  |  | ELCB |  |  | RCCB |  |  | 3 | Heater | B | Non-Cont | 17.3906 |  | MM2
Size(Amp) | 25 |  | Size(Amp) | 0 |  | Size(Amp) | 20 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  | Size(Amp) | 0 |  |  | Drive | C | Max.MCCB | 25 | 50
Type | C Type |  | Type | 0 |  | Type | C Type |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  | Type | 0 |  |  | A.C | C | NEC | 40.9691 | 50
Triping(Amp) | 188.6285 |  | Triping(Amp) | 0 |  | Triping(Amp) | 173.9058 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  | Triping(Amp) | 0 |  |  | Motor | C | Total Amp | 36.2534
Sen.I∆n | I∆n:30ma |  | Sen.I∆n |  |  | Sen.I∆n |  |  | Sen.I∆n |  |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n |  |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  | Sen.I∆n | I∆n:30ma |  |  | Ballast | C
Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  | Pole | 3 or 4 |  |  | Ind.Load | C | [6 empty] | D Type
[46 empty] | T.C | D |  |  | NEC | Amp | MCCB |  | 3
Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK |  | Cable selection | OK | [5 empty] | Cont | 23.5786 | 18.8628 | 25 | C Type | 2
Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 | Size(mm2) |  | 10 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 3
Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  | Length (mt) |  |  |  | MCB |  |  | Non-Cont | 17.3906 | 17.3906 | 20 | C Type | 2
Max.Length | 760 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  | Max.Length | 0 |  |  | MCCB |  |  | 0 | 0 | 0 | 0 | 0 | 3
[46 empty] | RCB |  |  | 0 | 0 | 0 | 0 | 0 | 3
[46 empty] | ELCB |  |  | 0 | 0 | 0 | 0 | 0 | 3
[46 empty] | RCCB |  |  | 0 | 0 | 0 | 0 | 0 | 3
Load | 18.9Amp |  | Load | 0Amp |  | Load | 17.4Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp |  | Load | 0Amp | [5 empty] | 0 | 0 | 0 | 0 | 0 | 3
[49 empty] | 0 | 0 | 0 | 0 | 0 | 3
Ph | 3 |  | Ph |  |  | Ph | 3 |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph |  |  | Ph | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3
Volt | 440 |  | Volt |  |  | Volt | 415 |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt |  |  | Volt | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3
Kw | 5.5 |  | Kw |  |  | Kw | 10 |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw |  |  | Kw | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3
Fur.Kw | 6 |  | Fur.Kw |  |  | Fur.Kw | 0 |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw |  |  | Fur.Kw | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3
Total Kw | 11.5 |  | Total Kw | 0 |  | Total Kw | 10 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 |  | Total Kw | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 3
P.F | 0.8 |  | P.F |  |  | P.F | 0.8 |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F |  |  | P.F | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3
Amp | 18.8628 |  | Amp | 0 |  | Amp | 17.3906 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0 |  | Amp | 0
Type | A.C |  | Type |  |  | Type | Motor |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type |  |  | Type
Natur. | Cont |  | Natur. |  |  | Natur. | Non-Cont |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur. |  |  | Natur.
NEC Amp | 23.5786 |  | NEC Amp | 0 |  | NEC Amp | 17.3906 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0 |  | NEC Amp | 0
Select: MCB/MCCB/ELCB/RCCB

## Data
| STANDARD MOTOR RATINGS | FLPF | 3/4THPF | FLEFF | 3/4THEFF |  | CABLE DATA
1 | 0.18 | 0.65 | 0.58 | 0.5 | 0.46 |  |  | CURRENT RATING AT 40 DEG (LAID IN TUNNEL)
2 | 0.22 | 0.6 | 0.55 | 0.58 | 0.53 |  |  | X-SECTION | PVC |  | HRPVC |  | LT XLPE |  | HT XLPE -upto 6.6kv(E) |  | EPR CSP
3 | 0.37 | 0.64 | 0.58 | 0.65 | 0.58 |  |  |  | AL | CU | AL | CU | AL | CU | AL | CU | CU
4 | 0.55 | 0.7 | 0.64 | 0.72 | 0.67 |  | 1 | 3cx1.5 | 14 | 17 | 16 | 21
5 | 0.75 | 0.7 | 0.65 | 0.74 | 0.69 |  | 2 | 3cx2.5 | 18 | 24 | 22 | 29 |  |  |  |  | 26.24
6 | 1.1 | 0.76 | 0.7 | 0.75 | 0.7 |  | 3 | 3cx4 | 23 | 30 | 28 | 37 | 31 | 36 |  |  | 35.26
7 | 1.5 | 0.79 | 0.72 | 0.77 | 0.72 |  | 4 | 3cx6 | 30 | 39 | 37 | 48 | 50 | 47 |  |  | 45.92
8 | 2.2 | 0.82 | 0.76 | 0.8 | 0.75 |  | 5 | 3cx10 | 39 | 57 | 49 | 63 | 67 | 62 |  |  | 63.96
9 | 3.7 | 0.83 | 0.78 | 0.82 | 0.81 |  | 6 | 3cx16 | 50 | 65 | 62 | 81 | 70 | 79 |  |  | 85.28
10 | 5.5 | 0.84 | 0.79 | 0.85 | 0.83 |  | 7 | 3cx25 | 63 | 66 | 85 | 110 | 96 | 108 | 100 | 115 | 113.98
11 | 7.5 | 0.85 | 0.81 | 0.87 | 0.87 |  | 8 | 3cx35 | 77 | 110 | 105 | 134 | 117 | 132 | 121 | 140 | 140.22
12 | 9.3 | 0.85 | 0.81 | 0.88 | 0.88 |  | 9 | 3cx50 | 95 | 135 | 128 | 165 | 142 | 162 | 145 | 175 | 174.66
13 | 11 | 0.85 | 0.82 | 0.89 | 0.89 |  | 10 | 3cx70 | 130 | 155 | 159 | 201 | 179 | 198 | 181 | 215 | 215.66
14 | 15 | 0.86 | 0.83 | 0.9 | 0.9 |  | 11 | 3cx95 | 155 | 200 | 189 | 244 | 221 | 240 | 221 | 255 | 259.94
15 | 18.5 | 0.86 | 0.84 | 0.91 | 0.91 |  | 12 | 3cx120 | 180 | 230 | 220 | 281 | 257 | 276 | 254 | 290 | 303.4
16 | 22 | 0.87 | 0.84 | 0.91 | 0.91 |  | 13 | 3cx150 | 205 | 255 | 250 | 323 | 292 | 318 | 290 | 335 | 348.5
17 | 30 | 0.89 | 0.86 | 0.92 | 0.92 |  | 14 | 3cx185 | 240 | 305 | 293 | 372 | 337 | 366 | 330 | 370 | 397.7
18 | 37 | 0.9 | 0.89 | 0.925 | 0.925 |  | 15 | 3cx225 | 255 | 335 | 323 | 407 | 379 | 402 | 369 | 415 | 371.77
19 | 45 | 0.9 | 0.89 | 0.93 | 0.93 |  | 16 | 3cx240 | 280 | 355 | 342 | 433 | 399 | 426 | 390 | 440 | 347.5306
20 | 55 | 0.86 | 0.82 | 0.935 | 0.935 |  | 17 | 3cx300 | 315 | 400 | 384 | 488 | 455 | 480 | 450 | 505 | 324.8716
21 | 75 | 0.89 | 0.88 | 0.94 | 0.94 |  | 18 | 3cx400 | 375 | 455 | 458 | 555 | 530 | 546 | 525 | 600 | 303.6899
22 | 90 | 0.9 | 0.86 | 0.945 | 0.945 |  | 19 | 3cx500 | 425 | 521 | 519 | 635 | 612 | 611.52 | 609 | 714 | 283.8894
23 | 110 | 0.9 | 0.86 | 0.945 | 0.945 |  | 20 | 3cx630 | 480 | 674 | 586 | 759 | 707 | 684.9024 | 706.44 | 849.66 | 265.3798
24 | 132 | 0.9 | 0.86 | 0.948 | 0.948 |  | 21 | 1cx120 | 220 | 280 | 268 | 342 | 268 | 336 | 277 | 368 | 298.5456
25 | 160 | 0.9 | 0.86 | 0.953 | 0.953 |  | 22 | 1cx150 | 250 | 320 | 305 | 390 | 309 | 384 | 318 | 422 | 342.924
26 | 180 | 0.9 | 0.86 | 0.953 | 0.953 |  | 23 | 1cx185 | 290 | 370 | 354 | 451 | 360 | 444 | 370 | 490 | 391.3368
27 | 200 | 0.9 | 0.86 | 0.955 | 0.955 |  | 24 | 1cx225 | 315 | 400 | 390 | 483 | 408 | 479 | 412 | 547 | 365.8216
28 | 225 | 0.87 | 0.82 | 0.948 | 0.94 |  | 25 | 1cx240 | 335 | 425 | 409 | 519 | 433 | 510 | 440 | 580 | 341.9701
29 | 250 | 0.87 | 0.82 | 0.945 | 0.935 |  | 26 | 1cx300 | 380 | 475 | 464 | 580 | 501 | 570 | 509 | 665 | 319.6736
[7 empty] | 27 | 1cx400 | 435 | 550 | 531 | 671 | 596 | 660 | 600 | 805 | 298.8309
[7 empty] | 28 | 1CX500 | 480 | 590 | 586 | 720 | 693 | 708 | 700 | 900 | 279.3471
[7 empty] | 29 | 1cx630 | 550 | 660 | 671 | 805 | 814 | 825 | 817 | 1030 | 261.1337
| CABLE DATA | [11 empty] | CABLE DATA
|  | CONDUCTOR RESISTANCE AT 70 DEG | [11 empty] | CONDUCTOR REACTANCE AT 50 Hz
| X-SECTION | PVC |  | HRPVC |  | LT XLPE |  | HT XLPE -upto 6.6kv(E) |  | EPR CSP |  |  | X-SECTION | PVC |  | HRPVC |  | LT XLPE |  | HT XLPE -upto 6.6kv(E) |  | EPR CSP
|  | AL | CU | AL | CU | AL | CU | AL | CU | CU |  |  |  | AL | CU | AL | CU | AL | CU | AL | CU | CU
1 | 3cx1.5 | 21.747 | 14.48 | 21.72 | 12.2 | 23.17 | 15.5 |  |  |  |  | 1 | 3cx1.5 | 0.126 | 0.119 | 0.092 | 0.109 | 0.107 | 0.107 |  |  | 0.116
2 | 3cx2.5 | 14.538 | 8.87 | 14.52 | 7.56 | 15.5 | 9.48 |  |  | 8.21 |  | 2 | 3cx2.5 | 0.119 | 0.115 | 0.087 | 0.105 | 0.0985 | 0.0985 |  |  | 0.109
3 | 3cx4 | 8.903 | 5.52 | 8.89 | 4.7 | 9.48 | 5.9 |  |  | 5.09 |  | 3 | 3cx4 | 0.116 | 0.112 | 0.081 | 0.101 | 0.0927 | 0.0927 |  |  | 0.106
4 | 3cx6 | 5.539 | 3.685 | 5.53 | 3.11 | 5.9 | 3.94 |  |  | 3.39 |  | 4 | 3cx6 | 0.11 | 0.104 | 0.073 | 0.0949 | 0.0884 | 0.0884 |  |  | 0.1
5 | 3cx10 | 3.701 | 2.19 | 3.7 | 1.84 | 3.94 | 2.34 |  |  | 1.95 |  | 5 | 3cx10 | 0.1 | 0.099 | 0.064 | 0.089 | 0.0837 | 0.0837 |  |  | 0.096
6 | 3cx16 | 2.295 | 1.376 | 2.29 | 1.16 | 2.44 | 1.47 |  |  | 1.24 |  | 6 | 3cx16 | 0.097 | 0.09 | 0.055 | 0.0858 | 0.0808 | 0.0808 |  |  | 0.091
7 | 3cx25 | 1.442 | 0.87 | 1.44 | 0.734 | 1.54 | 0.93 | 1.54 | 0.93 | 0.795 |  | 7 | 3cx25 | 0.097 | 0.088 | 0.054 | 0.0842 | 0.0805 | 0.0805 | 0.116 | 0.116 | 0.088
8 | 3cx35 | 1.043 | 0.627 | 1.042 | 0.529 | 1.11 | 0.671 | 1.11 | 0.671 | 0.565 |  | 8 | 3cx35 | 0.097 | 0.086 | 0.05 | 0.0824 | 0.0783 | 0.0783 | 0.111 | 0.111 | 0.086
9 | 3cx50 | 0.77 | 0.463 | 0.77 | 0.391 | q | 0.495 | 0.82 | 0.495 | 0.393 |  | 9 | 3cx50 | 0.094 | 0.086 | 0.05 | 0.0794 | 0.075 | 0.075 | 0.104 | 0.104 | 0.082
10 | 3cx70 | 0.532 | 0.321 | 0.532 | 0.27 | 0.567 | 0.343 | 0.567 | 0.343 | 0.277 |  | 10 | 3cx70 | 0.09 | 0.083 | 0.046 | 0.0764 | 0.074 | 0.074 | 0.1 | 0.1 | 0.079
11 | 3cx95 | 0.384 | 0.231 | 0.385 | 0.195 | 0.41 | 0.247 | 0.41 | 0.247 | 0.21 |  | 11 | 3cx95 | 0.09 | 0.083 | 0.043 | 0.0761 | 0.0724 | 0.0724 | 0.095 | 0.095 | 0.077
12 | 3cx120 | 0.304 | 0.183 | 0.304 | 0.154 | 0.324 | 0.196 | 0.324 | 0.196 | 0.164 |  | 12 | 3cx120 | 0.087 | 0.082 | 0.042 | 0.0738 | 0.0712 | 0.0712 | 0.092 | 0.092 | 0.076
13 | 3cx150 | 0.248 | 0.148 | 0.248 | 0.126 | 0.264 | 0.159 | 0.264 | 0.159 | 0.132 |  | 13 | 3cx150 | 0.087 | 0.082 | 0.042 | 0.0738 | 0.0716 | 0.0716 | 0.089 | 0.089 | 0.076
14 | 3cx185 | 0.197 | 0.119 | 0.198 | 0.1 | 0.21 | 0.127 | 0.21 | 0.127 | 0.108 |  | 14 | 3cx185 | 0.087 | 0.082 | 0.042 | 0.0738 | 0.0718 | 0.0718 | 0.087 | 0.087 | 0.076
15 | 3cx240 | 0.15 | 0.0902 | 0.152 | 0.0762 | 0.16 | 0.096 | 0.16 | 0.096 | 0.0817 |  | 15 | 3cx240 | 0.087 | 0.079 | 0.041 | 0.0732 | 0.071 | 0.071 | 0.085 | 0.085 | 0.075
16 | 3cx300 | 0.12 | 0.0719 | 0.122 | 0.0607 | 0.128 | 0.077 | 0.13 | 0.077 | 0.0654 |  | 16 | 3cx300 | 0.086 | 0.079 | 0.04 | 0.0729 | 0.0705 | 0.0705 | 0.082 | 0.082 | 0.075
17 | 3cx400 | 0.0935 | 0.0562 | 0.0962 | 0.0475 | 0.1 | 0.06 | 0.1 | 0.06 | 0.04 |  | 17 | 3cx400 | 0.086 | 0.079 | 0.04 | 0.0725 | 0.0704 | 0.0704 | 0.079 | 0.079 | 0.075
18 | 3cx500 | 0.0727 | 0.0438 | 0.0762 | 0.0369 | 0.077 | 0.047 | 0.0774 | 0.047 | 0.0391 |  | 18 | 3cx500 | 0.079 | 0.079 | 0.04 | 0.0727 | 0.0702 | 0.0702 | 0.073 | 0.073 | 0.075
19 | 3cx630 | 0.0564 | 0.0339 | 0.0608 | 0.0286 | 0.06 | 0.036 | 0.06 | 0.036 | 0.0306 |  | 19 | 3cx630 | - | - | 0.04 | 0.725 | 0.0698 | 0.0698 | 0.068 | 0.068 | 0.074
20 | 1cx120 |  |  | 0.304 | 0.154 | 0.324 | 0.196 | 0.324 | 0.196 | 0.164 |  | 20 | 1cx120 | 0.087 | 0.0738 | 0.08 | 0.0738 | 0.0968 | 0.0968 | 0.092 | 0.092 | 0.075
21 | 1cx150 |  |  | 0.248 | 0.126 | 0.264 | 0.159 | 0.264 | 0.159 | 0.132 |  | 21 | 1cx150 | 0.086 | 0.0738 | 0.082 | 0.0738 | 0.0941 | 0.0941 | 0.089 | 0.089 | 0.075
22 | 1cx185 |  |  | 0.198 | 0.1 | 0.21 | 0.127 | 0.21 | 0.127 | 0.108 |  | 22 | 1cx185 | 0.085 | 0.0738 | 0.079 | 0.0738 | 0.0932 | 0.0932 | 0.087 | 0.087 | 0.075
23 | 1cx225 |  |  | 0.171 | 0.85 | 0.18 | 0.107 | 0.18 | 0.11 | 0.093 |  | 23 | 1cx225 | 0.084 | 0.0735 | 0.077 | 0.0735 | 0.0911 | 0.0911 | 0.086 | 0.086 | 0.075
24 | 1cx240 |  |  | 0.152 | 0.0762 | 0.16 | 0.096 | 0.16 | 0.096 | 0.0817 |  | 24 | 1cx240 | 0.083 | 0.0732 | 0.075 | 0.0732 | 0.09 | 0.09 | 0.085 | 0.085 | 0.074
25 | 1cx300 |  |  | 0.122 | 0.0607 | 0.128 | 0.077 | 0.13 | 0.077 | 0.0654 |  | 25 | 1cx300 | 0.083 | 0.0729 | 0.072 | 0.0729 | 0.0881 | 0.0881 | 0.082 | 0.082 | 0.074
26 | 1cx400 |  |  | 0.0962 | 0.0475 | 0.1 | 0.06 | 0.1 | 0.06 | 0.04 |  | 26 | 1cx400 | 0.082 | 0.0725 | 0.07 | 0.0725 | 0.0873 | 0.0873 | 0.079 | 0.079 | 0.074
27 | 1CX500 |  |  | 0.0762 | 0.0369 | 0.077 | 0.047 | 0.0774 | 0.047 | 0.0391 |  | 27 | 1CX500 | 0.081 | 0.0727 | 0.069 | 0.0727 | 0.0859 | 0.0859 | 0.073 | 0.073 | 0.074
28 | 1cx630 |  |  | 0.0608 | 0.0286 | 0.06 | 0.036 | 0.06 | 0.036 | 0.0306 |  | 28 | 1cx630 | 0.081 | 0.725 | 0.067 | 0.725 | 0.0843 | 0.0843 | 0.068 | 0.068 | 0.073
| SYSTEM VOLTAGE |  | (Temp. Derating factor) | [5 empty] | No of Cable/Tray | (Grouping factor)==No of Tray
1 | 240 |  |  | PVC | HR PVC | HT XLPE | EPR CSP |  |  | 1 | 2 | 3 | 4 | 6 | 8
2 | 415 | 1 | 25 | 1.25 | 1.16 | 1.14 | 1.28 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1100 | 2 | 30 | 1.16 | 1.1 | 1.1 | 1.22 |  | 2 | 0.84 | 0.8 | 0.78 | 0.77 | 0.76 | 0.75 | 2
4 | 3300 | 3 | 35 | 1.09 | 1.05 | 1.04 | 1.134 |  | 3 | 0.8 | 0.76 | 0.74 | 0.73 | 0.72 | 0.71 | 3
5 | 6600 | 4 | 40 | 1 | 1 | 1 | 1 |  | 4 | 0.78 | 0.74 | 0.72 | 0.71 | 0.7 | 0.69 | 4
6 | 11000 | 5 | 45 | 0.9 | 0.94 | 0.95 | 0.975 |  | 5 | 0.77 | 0.73 | 0.7 | 0.69 | 0.68 | 0.67 | 6
7 | 33000 | 6 | 50 | 0.8 | 0.88 | 0.9 | 0.878 |  | 6 | 0.75 | 0.71 | 0.7 | 0.68 | 0.68 | 0.66 | 8
|  | 7 | 55 | 0.69 | 0.82 | 0.85 | 0.768 |  | 7 | 0.74 | 0.69 | 0.675 | 0.66 | 0.66 | 0.64
1 Ph |  | 8 | 60 | 0.62 | 0.74 | 0.8 | 0.658 |  | 8 | 0.73 | 0.69 | 0.68 | 0.67 | 0.66 | 0.64
3 Ph
| Current Rating |  |  |  | Corrrection Factor:K1 |  |  |  | Ground Corrrection Factor:K2 |  |  |  | Corrrection Factor:K3 |  |  |  | Correction Factor(K4)(Ground Cable Dist)
| CABLE TYPE | AL | CU | [9 empty] | Soil Thermal Resistivity: 2.5 k.m/W |  |  |  | No of Circuit | Nill | cable Dia | 0.125m | 0.25m | 0.5m
1 | PVC | #REF! | #REF! |  | Ambient Temp© | Insulation |  |  | Ground Temp© | Insulation |  |  | Resistivity | K3 |  |  | 1 | 1 | 1 | 1 | 1 | 1
2 | HR PVC | #REF! | #REF! |  |  | PVC | XLPE/EPR |  |  | PVC | XLPE/EPR |  | 1 | 1.18 |  |  | 2 | 0.75 | 0.8 | 0.85 | 0.9 | 0.9
3 | LT XLPE | #REF! | #REF! |  | 10 | 1.22 | 1.15 |  | 10 | 1.1 | 1.07 |  | 1.5 | 1.1 |  |  | 3 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85
4 | HT XLPE | #REF! | #REF! |  | 15 | 1.17 | 1.12 |  | 15 | 1.05 | 1.04 |  | 2 | 1.05 |  |  | 4 | 0.6 | 0.6 | 0.7 | 0.75 | 0.8
5 | EPR CSP | #REF! | #REF! |  | 20 | 1.12 | 1.08 |  | 20 | 0.95 | 0.96 |  | 2.5 | 1 |  |  | 5 | 0.55 | 0.55 | 0.65 | 0.7 | 0.8
[5 empty] | 25 | 1.06 | 1.04 |  | 25 | 0.89 | 0.93 |  | 3 | 0.96 |  |  | 6 | 0.5 | 0.55 | 0.6 | 0.7 | 0.8
| CONDUCTOR | current |  |  | 35 | 0.94 | 0.96 |  | 35 | 0.77 | 0.89
1 | AL | #REF! |  |  | 40 | 0.87 | 0.91 |  | 40 | 0.71 | 0.85 |  | Corrrection Factor:K3
2 | CU | #REF! |  |  | 45 | 0.79 | 0.87 |  | 45 | 0.63 | 0.8 |  | Nature of Soil | K3
[5 empty] | 50 | 0.71 | 0.82 |  | 50 | 0.55 | 0.76 |  | Very Wet Soil | 1.21
[5 empty] | 55 | 0.61 | 0.76 |  | 55 | 0.45 | 0.71 |  | Wet Soil | 1.13
|  | resistance |  |  | 60 | 0.5 | 0.71 |  | 60 | 0 | 0.65 |  | Damp Soil | 1.05
| CABLE TYPE | AL | CU |  | 65 | 0 | 0.65 |  | 65 | 0 | 0.6 |  | Dry Soil | 1
1 | PVC | #REF! | #REF! |  | 70 | 0 | 0.58 |  | 70 | 0 | 0.53 |  | Very Dry Soil | 0.86
2 | HRPVC | #REF! | #REF! |  | 75 | 0 | 0.5 |  | 75 | 0 | 0.46
3 | LT XLPE | #REF! | #REF! |  | 80 | 0 | 0.41 |  | 80 | 0 | 0.38
4 | HT XLPE | #REF! | #REF!
5 | EPR CSP | #REF! | #REF!
| CONDUCTOR | res.
1 | AL | #REF!
2 | CU | #REF!
reactance
| CABLE TYPE | AL | CU
1 | PVC | #REF! | #REF!
2 | HRPVC | #REF! | #REF!
3 | LT XLPE | #REF! | #REF!
4 | HT XLPE | #REF! | #REF!
5 | EPR CSP | #REF! | #REF!
| CONDUCTOR | reac.
1 | AL | #REF!
2 | CU | #REF!
NO. OF RUNS
1 | 1
2 | 2
3 | 3
4 | 4
5 | 5
6 | 6
7 | 7
8 | 8
9 | 9
10 | 10
11 | 11
12 | 12
13 | 13
14 | 14
15 | 15
16 | 16
17 | 17
18 | 18
19 | 19
20 | 20

## Sheet1
[7 empty] | MCCB/ELCB | Size
[7 empty] | 0.5 | 6
AWG | mm2 | Maximum Fuse Size(Amp) |  | AWG | mm2 |  | 1 | 6 | Max Amp |  | mm2 | AWG | 3cx1.5
OO | 70 | 400 |  | 26 | 0.13 |  | 2 | 6 | 2.2 | 2.7 | 0.13 | 26 | 3cx2.5
OO | 55 | 325 |  | 25 | 0.16 |  | 4 | 6 | 2.7 | 3.5 | 0.16 | 25 | 3cx4
1 | 50 | 250 |  | 24 | 0.2 |  | 6 | 10 | 3.5 | 2.7 | 0.2 | 24 | 3cx6
2 | 35 | 200 |  | 23 | 0.26 |  | 10 | 16 | 4.7 | 3.5 | 0.26 | 23 | 3cx10
4 | 25 | 125 |  | 22 | 0.33 |  | 16 | 20 | 7 | 4.7 | 0.33 | 22 | 3cx16
6 | 16 | 80 |  | 21 | 0.41 |  | 20 | 25 | 9 | 7 | 0.41 | 21 | 3cx25
8 | 10 | 50 |  | 20 | 0.52 |  | 25 | 32 | 11 | 9 | 0.52 | 20 | 3cx35
10 | 6 | 30 |  | 19 | 0.65 |  | 32 | 40 | 14 | 11 | 0.65 | 19 | 3cx50
12 | 4 | 20 |  | 18 | 0.82 |  | 40 | 45 | 16 | 14 | 0.82 | 18 | 3cx70
14 | 2.5 | 15 |  | 17 | 1.04 |  | 45 | 50 | 19 | 16 | 1.04 | 17 | 3cx95
16 | 1.5 | 7.5 |  | 16 | 1.5 |  | 50 | 63 | 22 | 19 | 1.5 | 16 | 3cx120
|  |  |  | 14 | 2.5 |  | 63 | 80 | 32 | 22 | 2.5 | 14 | 3cx150
|  |  |  | 12 | 4 |  | 80 | 100 | 41 | 32 | 4 | 12 | 3cx185
Factor of Max.Utilization | Ku |  |  | 10 | 6 |  | 100 | 125 | 55 | 41 | 6 | 10 | 3cx225
Motor | 0.75 |  |  | 8 | 10 |  | 125 | 225 | 64 | 55 | 10 | 8
Ltg | 1 |  |  | 6 | 16 |  | 225 | 600 | 73 | 64 | 16 | 6
|  |  |  | 4 | 25 |  | 600 | 800 | 135 | 73 | 25 | 4
|  |  |  | 2 | 35 |  | 800 | 1600 | 181 | 135 | 35 | 2
Demand Factor | Ks |  |  | 1 | 50 |  | 1600 | 2000 | 211 | 181 | 50 | 1
Ltg | 1 |  |  | O | 55 |  | 2000 | 3000 | 245 | 211 | 55 | O
Heating/AC | 1 |  |  | OO | 70 |  | 3000 | 3200 | 283 | 245 | 70 | OO
Power Socket | 2 |  |  | OOO | 95 |  | 3200 | 4000 | 328 | 283 | 95 | OOO
Lift/Hoist | 0.6 to 1 |  |  | OOOO | 120 |  | 4000 | 5000 | 380 | 328 | 120 | OOOO
Motor | 0.6 | [5 empty] | 5000 | 6000 |  | 380 | 120
[7 empty] | 6000 | 6000
Maximum Circuit Length in mtr for Cu conductor ( for Alu multiply 0.62)
Operating Cuurent Im of the Instantaneous Tripping element(A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
50 | 100 | 167 | 267 | 400
63 | 79 | 133 | 212 | 317
80 | 63 | 104 | 167 | 250 | 417
100 | 50 | 83 | 133 | 200 | 333
125 | 40 | 67 | 107 | 160 | 267 | 427
160 | 31 | 52 | 83 | 125 | 208 | 333
200 | 25 | 42 | 67 | 100 | 167 | 267 | 417
250 | 20 | 33 | 53 | 80 | 133 | 213 | 333 | 467
320 | 16 | 26 | 42 | 63 | 104 | 167 | 260 | 365 | 495
400 | 13 | 21 | 33 | 50 | 83 | 133 | 208 | 292 | 396
500 | 10 | 17 | 27 | 40 | 67 | 107 | 167 | 233 | 317
560 | 9 | 15 | 24 | 36 | 60 | 95 | 149 | 208 | 283 | 417
630 | 8 | 13 | 21 | 32 | 63 | 85 | 132 | 185 | 251 | 370
700 | 7 | 12 | 19 | 29 | 48 | 76 | 119 | 167 | 226 | 333 | 452
800 | 6 | 10 | 17 | 25 | 42 | 67 | 104 | 146 | 198 | 292 | 396
875 | 6 | 10 | 15 | 23 | 38 | 61 | 95 | 133 | 181 | 267 | 362 | 457
1000 | 5 | 8 | 13 | 20 | 33 | 53 | 83 | 117 | 158 | 233 | 317 | 400 | 435
1120 | 4 | 7 | 12 | 18 | 30 | 48 | 74 | 104 | 141 | 208 | 283 | 357 | 388 | 459
1250 | 4 | 7 | 11 | 16 | 27 | 43 | 67 | 94 | 127 | 187 | 253 | 320 | 348 | 411
1600 |  | 5 | 8 | 13 | 21 | 33 | 52 | 73 | 99 | 146 | 198 | 250 | 272 | 321 | 400
2000 |  | 4 | 7 | 10 | 17 | 27 | 42 | 58 | 79 | 117 | 158 | 200 | 217 | 257 | 320
2500 |  |  | 5 | 8 | 13 | 21 | 33 | 47 | 63 | 93 | 127 | 160 | 174 | 206 | 256
3200 |  |  | 4 | 6 | 11 | 17 | 26 | 36 | 49 | 73 | 99 | 125 | 136 | 161 | 200
4000 |  |  |  | 5 | 8 | 13 | 21 | 29 | 40 | 58 | 79 | 100 | 109 | 128 | 160
5000 |  |  |  | 4 | 7 | 11 | 17 | 23 | 32 | 47 | 63 | 80 | 87 | 103 | 128
6300 |  |  |  |  | 5 | 8 | 13 | 19 | 25 | 37 | 50 | 63 | 69 | 82 | 102
8000 |  |  |  |  | 4 | 7 | 10 | 16 | 20 | 29 | 40 | 50 | 54 | 64 | 80
10000 | [5 empty] | 5 | 8 | 12 | 16 | 23 | 32 | 40 | 43 | 51 | 64
12500 | [5 empty] | 4 | 7 | 9 | 13 | 19 | 25 | 32 | 35 | 41 | 51
Maximum Length of Copper Conductor circuit in Meter protcted by B Type C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
6 | 200 | 333 | 533 | 800 | 0 | 0 | 0
10 | 120 | 200 | 320 | 480 | 800 | 0 | 0
16 | 75 | 125 | 200 | 300 | 500 | 800 | 0
20 | 60 | 100 | 160 | 240 | 400 | 640 | 0
25 | 48 | 80 | 128 | 192 | 320 | 512 | 800
32 | 37 | 62 | 100 | 150 | 250 | 400 | 625 | 875
40 | 30 | 50 | 80 | 120 | 200 | 320 | 500 | 700
50 | 24 | 40 | 64 | 96 | 160 | 256 | 400 | 560 | 760
63 | 19 | 32 | 51 | 76 | 127 | 203 | 317 | 444 | 603
80 | 15 | 25 | 40 | 60 | 100 | 160 | 250 | 350 | 475
100 | 12 | 20 | 32 | 48 | 80 | 128 | 200 | 280 | 380
125 | 10 | 16 | 26 | 38 | 64 | 102 | 160 | 224 | 304
Maximum Length of Copper Conductor circuit in Meter protcted by CType C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
6 | 100 | 167 | 267 | 400 | 667
10 | 60 | 100 | 160 | 240 | 400 | 640
16 | 37 | 62 | 100 | 150 | 250 | 400 | 625 | 875
20 | 30 | 50 | 80 | 120 | 200 | 320 | 500 | 700
25 | 24 | 40 | 64 | 96 | 160 | 256 | 400 | 560 | 760
32 | 18 | 31 | 50 | 75 | 125 | 200 | 313 | 438 | 594
40 | 15 | 25 | 40 | 60 | 100 | 160 | 250 | 350 | 475
50 | 12 | 20 | 32 | 48 | 80 | 128 | 200 | 280 | 380
63 | 9.5 | 16 | 26 | 38 | 64 | 102 | 159 | 222 | 302
80 | 7.5 | 12.5 | 20 | 30 | 50 | 80 | 125 | 175 | 238
100 | 6 | 10 | 16 | 24 | 40 | 64 | 100 | 140 | 190
125 | 5 | 8 | 13 | 19 | 32 | 51 | 80 | 112 | 152
Maximum Length of Copper Conductor circuit in Meter protcted by D Type C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
1 | 429 | 714
2 | 214 | 357 | 571 | 857
3 | 143 | 238 | 381 | 571 | 952
4 | 107 | 179 | 286 | 429 | 714
6 | 71 | 119 | 190 | 286 | 476 | 762
10 | 43 | 71 | 114 | 171 | 286 | 457 | 714
16 | 27 | 45 | 71 | 107 | 179 | 286 | 446 | 625 | 848
20 | 21 | 36 | 57 | 86 | 143 | 229 | 357 | 500 | 679
25 | 17 | 29 | 46 | 69 | 114 | 183 | 286 | 400 | 543
32 | 13 | 22 | 36 | 54 | 89 | 143 | 223 | 313 | 424
40 | 11 | 18 | 29 | 43 | 71 | 114 | 179 | 250 | 339
50 | 9 | 14 | 23 | 34 | 57 | 91 | 143 | 200 | 271
63 | 7 | 11 | 18 | 27 | 45 | 73 | 113 | 159 | 215
80 | 5 | 9 | 14 | 21 | 36 | 57 | 89 | 125 | 170
100 | 4 | 7 | 11 | 17 | 29 | 46 | 71 | 100 | 136
125 | 3 | 6 | 9 | 14 | 23 | 37 | 57 | 80 | 109
Short circuit Current at T.C Secondary
3 Ph T.C Rating (KVA) | Rated FLC(Amp) | ISC at Secondary
50 | 70 | 1391
100 | 139 | 2782
160 | 223 | 4452
200 | 278 | 5565
250 | 348 | 6956
315 | 448 | 8765
400 | 556 | 11130
500 | 696 | 13912
600 | 836 | 16714
700 | 975 | 19500
800 | 1115 | 22286
900 | 1254 | 25072
1000 | 1393 | 27860
1250 | 1741 | 34820
1500 | 1089 | 41780
2000 | 1786 | 55720
2500 | 3482 | 69640
3000 | 4179 | 83580

## Sheet6
"C" For Copper conductor. | [5 empty] | "C" For Allu conductor. |  |  |  |  | MCCB/ELCB
AWG/Kcmill | 3 Single Conductor |  | 3 Conductor Cable |  |  | AWG/Kcmill | 3 Single Conductor |  | 3 Conductor Cable |  | 0.5 | 1
| 600V |  | 600V |  |  |  | 600V |  | 600V |  | 1 | 2
| Steel | Nonmagnetic | Steel | Nonmagnetic |  |  | Steel | Nonmagnetic | Steel | Nonmagnetic | 2 | 4
14 | 389 | 389 | 389 | 389 |  | 14 | 237 | 237 | 237 | 237 | 4 | 6
12 | 617 | 617 | 617 | 617 |  | 12 | 376 | 376 | 376 | 376 | 6 | 10
10 | 981 | 982 | 982 | 982 |  | 10 | 599 | 599 | 599 | 599 | 10 | 16
8 | 1557 | 1559 | 1559 | 1560 |  | 8 | 951 | 952 | 952 | 952 | 16 | 20
6 | 2425 | 2430 | 2431 | 2433 |  | 6 | 1481 | 1482 | 1482 | 1482 | 20 | 32
4 | 3806 | 3826 | 3830 | 3838 |  | 4 | 2346 | 2350 | 2351 | 2353 | 32 | 45
3 | 4774 | 4811 | 4820 | 4833 |  | 3 | 2952 | 2961 | 2963 | 2966 | 45 | 50
2 | 5907 | 6044 | 5989 | 6087 |  | 2 | 3713 | 3730 | 3734 | 3740 | 50 | 63
1 | 7293 | 7493 | 7454 | 7579 |  | 1 | 4645 | 4678 | 4686 | 4699 | 63 | 80
O | 8925 | 9317 | 9210 | 9473 |  | O | 5777 | 5838 | 5852 | 5876 | 80 | 100
OO | 10755 | 11424 | 11245 | 11703 |  | OO | 7187 | 7301 | 7327 | 7373 | 100 | 225
OOO | 12844 | 13923 | 13656 | 14410 |  | OOO | 8826 | 9110 | 9077 | 9243 | 225 | 600
OOOO | 15082 | 16673 | 16392 | 17483 |  | OOOO | 10741 | 11174 | 11185 | 11409 | 600 | 800
250 kcmil | 16483 | 18594 | 18311 | 19779 |  | 250 kcmil | 12122 | 12862 | 12797 | 13236 | 800 | 1600
300 kcmil | 18177 | 20868 | 20617 | 22525 |  | 300 kcmil | 13910 | 14923 | 14917 | 15495 | 1600 | 2000
350 kcmil | 19704 | 22737 | 22646 | 24904 |  | 350 kcmil | 15484 | 16813 | 16795 | 17635 | 2000 | 3000
400 kcmil | 20566 | 24297 | 24253 | 26916 |  | 400 kcmil | 16671 | 18506 | 18462 | 19588 | 3000 | 3200
500 kcmil | 22185 | 26706 | 26980 | 30096 |  | 500 kcmil | 18756 | 21391 | 21395 | 23018 | 3200 | 4000
600 kcmil | 22965 | 28033 | 28752 | 32154 |  | 600 kcmil | 20093 | 23451 | 23633 | 25708 | 4000 | 5000
750 kcmil | 24137 | 29735 | 31051 | 34605 |  | 750 kcmil | 21766 | 25976 | 26432 | 29036 | 5000 | 6000
1000 kcmil | 25278 | 31491 | 33864 | 37197 |  | 1000 kcmil | 23478 | 28779 | 29865 | 32938 | 6000 | 6000
Maximum Length of Copper Conductor circuit in Meter protcted by B Type C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
6 | 200 | 333 | 533 | 800 | 0 | 0 | 0
10 | 120 | 200 | 320 | 480 | 800 | 0 | 0
16 | 75 | 125 | 200 | 300 | 500 | 800 | 0
20 | 60 | 100 | 160 | 240 | 400 | 640 | 0
25 | 48 | 80 | 128 | 192 | 320 | 512 | 800
32 | 37 | 62 | 100 | 150 | 250 | 400 | 625 | 875
40 | 30 | 50 | 80 | 120 | 200 | 320 | 500 | 700
50 | 24 | 40 | 64 | 96 | 160 | 256 | 400 | 560 | 760
63 | 19 | 32 | 51 | 76 | 127 | 203 | 317 | 444 | 603
80 | 15 | 25 | 40 | 60 | 100 | 160 | 250 | 350 | 475
100 | 12 | 20 | 32 | 48 | 80 | 128 | 200 | 280 | 380
125 | 10 | 16 | 26 | 38 | 64 | 102 | 160 | 224 | 304
Maximum Length of Copper Conductor circuit in Meter protcted by CType C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
6 | 100 | 167 | 267 | 400 | 667
10 | 60 | 100 | 160 | 240 | 400 | 640
16 | 37 | 62 | 100 | 150 | 250 | 400 | 625 | 875
20 | 30 | 50 | 80 | 120 | 200 | 320 | 500 | 700
25 | 24 | 40 | 64 | 96 | 160 | 256 | 400 | 560 | 760
32 | 18 | 31 | 50 | 75 | 125 | 200 | 313 | 438 | 594
40 | 15 | 25 | 40 | 60 | 100 | 160 | 250 | 350 | 475
50 | 12 | 20 | 32 | 48 | 80 | 128 | 200 | 280 | 380
63 | 9.5 | 16 | 26 | 38 | 64 | 102 | 159 | 222 | 302
80 | 7.5 | 12.5 | 20 | 30 | 50 | 80 | 125 | 175 | 238
100 | 6 | 10 | 16 | 24 | 40 | 64 | 100 | 140 | 190
125 | 5 | 8 | 13 | 19 | 32 | 51 | 80 | 112 | 152
Maximum Length of Copper Conductor circuit in Meter protcted by D Type C.B
Rated Current of C.B (A) | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50
1 | 429 | 714
2 | 214 | 357 | 571 | 857
3 | 143 | 238 | 381 | 571 | 952
4 | 107 | 179 | 286 | 429 | 714
6 | 71 | 119 | 190 | 286 | 476 | 762
10 | 43 | 71 | 114 | 171 | 286 | 457 | 714
16 | 27 | 45 | 71 | 107 | 179 | 286 | 446 | 625 | 848
20 | 21 | 36 | 57 | 86 | 143 | 229 | 357 | 500 | 679
25 | 17 | 29 | 46 | 69 | 114 | 183 | 286 | 400 | 543
32 | 13 | 22 | 36 | 54 | 89 | 143 | 223 | 313 | 424
40 | 11 | 18 | 29 | 43 | 71 | 114 | 179 | 250 | 339
50 | 9 | 14 | 23 | 34 | 57 | 91 | 143 | 200 | 271
63 | 7 | 11 | 18 | 27 | 45 | 73 | 113 | 159 | 215
80 | 5 | 9 | 14 | 21 | 36 | 57 | 89 | 125 | 170
100 | 4 | 7 | 11 | 17 | 29 | 46 | 71 | 100 | 136
125 | 3 | 6 | 9 | 14 | 23 | 37 | 57 | 80 | 109