## Infinitue Bus Method
N.B Calculation is made on Infinitue Bus Method
Fault Current Calculation | Jignesh.Parmar www.electricalnotes.wordpress.com
Fault Current at Transformer Primary Side (Enter This Value if You know otherwise leave blank) |  | Amp | Alu | 1 Core Cable | Non-Metalic
|  |  | Cu | 3 Core Cable | Metalic
Fault Current At Transformer |  |  | Yes
Transformer Kva | 3 | Kva | No
Secondary Voltage of Transformer (Line-Line) | 433 | Volt
Secondary Voltage of Transformer (Line-Neutral) | 250 | Volt
Transformer Impedance (Zt) | 6 | %
Transformer Secondary Full Load Current I (Line-Line) | 4.0002 | Amp
Transformer Secondary Full Load Current I (Line-Neutral) | 6.0004 | Amp
KVA Short Circuit At Primary Side
Source Impedance (Zu) | 0
Total Impedance (Z =Zu+Zt) | 0.06
Short Circuit Current RMS Symmetrical | 66.6706 | Amp
Fault Current At Transformer Secondary ( Isc(L-L)=I (L-L)/Total Impedance) | 66.6706 | Amp
Fault Current At Transformer Secondary ( Isc(L-N)=I (L-N)/Total Impedance) | 100.0059 | Amp
Fault Current At Main Panel
Cable Length from Transformer to Main Panel | 50 | Meter
Type of Cable | Cu | 3 Core Cable
No of Conductor/Phase | 1
Size of Phase Conductor | 120 mm2
Size of Neutral Conductor | 120 mm2
Type of Race Way | Non-Metalic
Phase Conductor Constant (C1) | 17483
Neutral Conductor Constant (C2) | 17483
F1(L-L) [F(L-L)=(1.732 X Length X Isc)/(C1 X No of Conductor X Volt)] | 0.00076269
F2(L-N) [F(L-L)=(1.732 X Length X Isc)/(C2 X No of Conductor X Volt)] | 0.0019815
M1(L-L) [M=(1/(1+F1)] | 0.99924
M2(L-N) [M=(1/(1+F2)] | 0.99802
Fault Current at Main Panel Disconnection (L-L) [Isc X M1] | 66.6198 | Amp
Fault Current at Main Panel Disconnection (L-N) [Isc X M2] | 99.8081 | Amp
Fault Current At Sub Panel
Cable Length from Main Panel to Sub Panel | 20 | Meter
Type of Cable | Cu | 3 Core Cable
No of Conductor/Phase | 1
Size of Phase Conductor | 30 mm2
Size of Neutral Conductor | 127 mm2
Type of Race Way | Non-Metalic
Phase Conductor Constant (C1) | 4833
Neutral Conductor Constant (C2) | 19779
F1(L-L) [F(L-L)=(1.732 X Length X Isc)/(C1 X No of Conductor X Volt)] | 0.0011027
F2(L-N) [F(L-L)=(1.732 X Length X Isc)/(C2 X No of Conductor X Volt)] | 0.00040369
M1(L-L) [M=(1/(1+F1)] | 0.9989
M2(L-N) [M=(1/(1+F2)] | 0.9996
Fault Current at Sub Panel Disconnection (L-L) [Isc X M1] | 66.5464 | Amp
Fault Current at Sub Panel Disconnection (L-N) [Isc X M2] | 99.7678 | Amp
Fault Current At Distribution Board
Cable Length from Sub Panel to Distribution Board | 50 | Meter
Type of Cable | Cu | 1 Core Cable
No of Conductor/Phase | 1
Size of Phase Conductor | 127 mm2
Size of Neutral Conductor | 127 mm2
Type of Race Way | Non-Metalic
Phase Conductor Constant (C1) | 18594
Neutral Conductor Constant (C2) | 18594
F1(L-L) [F(L-L)=(1.732 X Length X Isc)/(C1 X No of Conductor X Volt)] | 0.00071578
F2(L-N) [F(L-L)=(1.732 X Length X Isc)/(C2 X No of Conductor X Volt)] | 0.0010731
M1(L-L) [M=(1/(1+F1)] | 0.99928
M2(L-N) [M=(1/(1+F2)] | 0.99893
Fault Current at Distribution Board Disconnection (L-L) [Isc X M1] | 66.4988 | Amp
Fault Current at Distribution Board Disconnection (L-N) [Isc X M2] | 99.6609 | Amp
Note on D5: Insert Fault Current Provided by Governing Utility here. If You enter This Valur than KVA of T/C and Impedance is not required for Further Calculation

## Base MVA Method
Fault Current Calculation |  |  | Jignesh.Parmar www.electricalnotes.wordpress.com , jiguparmar@yahoo.com
Calculating Fault Current | [5 empty] | Calculation Results
PVC Flexible (Up to 1.1 KV)
Fault Level at Incoming Site | 360 | MVA |  |  |  | Fault Level at Incoming Site | 360 | MVA | LT PVC (Up to 1.1 KV) | 1cX25 | 1cX 95 | 1cX4 | 1cX0.5
Base MVA (For H.T beaker and Transformer Primary side) | 3 | MVA |  |  |  | Fault Level at H.T Side Diesel / Gas Generator | 25.1916 | MVA | LT XLPE (Up to 1.1 KV) | 1cX35 | 1cX120 | 1cX6 | 1cX0.75
Base KV (For H.T beaker and Transformer Primary side) | 11 | KV |  |  |  | Fault Level at Transformer Primary Side | 25.1181 | MVA | HT XLPE ( 6.6 KV-Earthed) | 1cX50 | 1cX150 | 1cX10 | 1cX1
Base KV (For Transformer Secondary,LT Panel,D.B) | 0.433 | KV |  |  |  | Fault Level at Transformer Secondary Side | 8.1329 | MVA | HT XLPE ( 11 KV-Earthed) | 1cX70 | 1cX185 | 1cX16 | 1cX1.5
[6 empty] | Fault Current at Transformer Secondary | 10.8445 | Kamp | HT XLPE ( 11 KV-Un Earthed) | 1cX95 | 1cX240 | 1cX25 | 1cX2.5
Fault Level at HT Sub Station Side | [5 empty] | Fault Level at Main LT Panel | 4.6051 | MVA | HT XLPE ( 66 KV-Earthed) | 1cX120 | 1cX300 | 1cX35 | 1cX4
[6 empty] | Fault Current at Main LT Panel | 6.1405 | Kamp | AL | 1cX150 | 1cX400 | 1cX50 | 1cX6
P.U Reactance at Incoming of H.T Breaker [Z p.u(A) ] | 0.0083333 | Ω |  |  |  | Fault Level at LT Sub Panel | 3.7534 | MVA | CU | 1cX185 | 1cX 500 | 1cX70 | 1cX10
Fault Level at Diesel / Gas Generator | [5 empty] | Fault Current at LT Sub Panel | 5.0049 | Kamp | 1 | 1cX240 | 1cX 630 | 1cX95 | 1cX16
[6 empty] | Fault Level at Distribution Board | 0.36388 | MVA |  | 1cX300 | 1cX800 | 1cX120 | 1cX25
Size of Cable from Generator To H.T Sub Station | HT XLPE ( 6.6 KV-Earthed) | CU | 1cX35 | 1 | Runs | Fault Current at Distribution Board | 0.48521 | Kamp |  | 1cX400 | 1cX1000 | 1cX150 | 1cX35
Length of Cable from Generator To H.T Sub Station | 100 | Meter | [7 empty] | 1cX 500 |  | 1cX185 | 1cX50
R (D.G) | 1.1 | Ω/Km |  |  |  | N.B: Calculation is based on Base KVA Method |  |  |  | 1cX 630 |  | 1cX240 | 1cX70
X (D.G) | 0.129 | Ω/Km | [7 empty] | 1cX800 |  | 1cX300 | 1cX95
R (D.G) | 0.11 | Ω | [7 empty] | 1cX1000 |  | 1cX400 | 1cX120
X (D.G) | 0.0129 | Ω | [7 empty] | 3cX 25 |  | 1cX 500 | 2cX0.5
Z P.U (B) | 0.11075 | Ω | [7 empty] | 3cX 35 |  | 1cX 630 | 2cX0.75
Total Z p.u (Z p.u(A) + Z p.u(B) | 0.11909 | Ω | [7 empty] | 3cX 50 |  | 1cX800 | 2cX1
Fault Level at H.T Side Diesel / Gas Generator | 25.1916 | MVA | [7 empty] | 3cX 70 |  | 1cX1000 | 2cX1.5
[10 empty] | 3cX 95 |  | 2cX1.5 | 2cX2.5
Fault Level at Transformer Side | [9 empty] | 3cX 120 |  | 2cX2.5 | 2cX4
Transformer Rating | 1.5 | MVA | [7 empty] | 3cX 150 |  | 2cX4 | 3cX0.5
Transformer Impedance | 6.5 | % | [7 empty] | 3cX 185 |  | 2cX 6 | 3cX0.75
Size of Cable from H.T Breaker To Transformer | HT XLPE ( 11 KV-Un Earthed) | CU | 3cX 400 | 1 | Runs |  |  |  |  | 3cX 240 |  | 2cX10 | 3cX1
Length of Cable from H.T Breaker To Transformer | 100 | Meter | [7 empty] | 3cX 300 |  | 2cX16 | 3cX1.5
R (T/C) | 0.102 | Ω/Km |  |  | Ω/Km |  |  |  |  | 3cX 400 |  | 2cX25 | 3cX2.5
X (T/C) | 0.0968 | Ω/Km |  |  | Ω/Km | [6 empty] | 2cX35 | 3cX4
R (T/C) | 0.0102 | Ω | [9 empty] | 2cX50
X (T/C) | 0.00968 | Ω | [9 empty] | 2cX70
Z(T/C) | 0.014062 | Ω | [9 empty] | 2cX95
Z p.u (C) | 0.00034865 | Ω | [9 empty] | 2cX120
Total Z p.u (D) (Up to Transformer Primary) | 0.11944 | Ω | [9 empty] | 2cX150
Fault Level at Transformer Primary Side | 25.1181 | MVA | [9 empty] | 2cX185
% Reactance at Base KVA | 6.5 | % | [9 empty] | 2cX240
Z P.U (T/C) | 0.065 | Ω | [9 empty] | 2cX300
Total P.U Impedance up to T/C Secondary | 0.18444 | Ω | [9 empty] | 2cX400
Fault Level at Transformer Secondary Side | 8.1329 | MVA | [9 empty] | 2cX500
Fault Current at Transformer Secondary | 10.8445 | Kamp | [9 empty] | 2cX630
Fault Level at LT Sub Station Side | [11 empty] | 3cX1.5
Fault Level at Main LT Panel Side | [11 empty] | 3cX2.5
Size of Cable from Transformer To Main LT Panel | LT XLPE (Up to 1.1 KV) | CU | 3cX 95 | 1 | Runs | [6 empty] | 3cX4
Length of Cable from Transformer To Main LT Panel | 100 | Meter | [9 empty] | 3cX 6
R (Main LT) | 0.247 | Ω/Km |  |  | Ω/Km | [6 empty] | 3cX 10
X (Main LT) | 0.074 | Ω/Km |  |  | Ω/Km | [6 empty] | 3cX 16
R (Main LT) | 0.0247 | Ω | [9 empty] | 3cX 25
X (Main LT) | 0.0074 | Ω | [9 empty] | 3cX 35
Z (D) | 0.025785 | Ω | [9 empty] | 3cX 50
Z p.u (D) | 0.20629 | Ω | [9 empty] | 3cX 70
Total Z p.u (D) (Up to LT Main Panel) | 0.32573 | Ω | [9 empty] | 3cX 95
Fault Level at Main LT Panel | 4.6051 | MVA | [9 empty] | 3cX 120
Fault Current at Main LT Panel | 6.1405 | Kamp | [9 empty] | 3cX 150
3cX 185
Fault Level at LT Sub Panel Side | [11 empty] | 3cX 240
Size of Cable from Main LT Panel To LT Sub Panel | LT XLPE (Up to 1.1 KV) | CU | 3.5X50 | 1 | Runs | [6 empty] | 3cX 300
Length of Cable from Main LT Panel To LT Sub Panel | 100 | Meter | [9 empty] | 3cX 400
R (LT Sub) | 0.0495 | Ω/Km |  |  | Ω/Km | [6 empty] | 3cX 500
X (LT Sub) | 0.078 | Ω/Km |  |  | Ω/Km | [6 empty] | 3cX 630
R (LT Sub) | 0.00495 | Ω | [9 empty] | 3.5X16
X (LT Sub) | 0.0078 | Ω | [9 empty] | 3.5X25
Z (E) | 0.0092381 | Ω | [9 empty] | 3.5X35
Z p.u (E) | 0.073909 | Ω | [9 empty] | 3.5X50
Total Z p.u (D) (Up to LT Sub Panel) | 0.39963 | Ω | [9 empty] | 3.5X70
Fault Level at LT Sub Panel | 3.7534 | MVA | [9 empty] | 3.5X95
Fault Current at LT Sub Panel | 5.0049 | Kamp | [9 empty] | 3.5X120
3.5X150
Fault Level at Distribution Board Side | [11 empty] | 3.5X185
Size of Cable from LT Sub Panel To Distribution Board | PVC Flexible (Up to 1.1 KV) | CU | 1cX4 | 1 | Runs | [6 empty] | 3.5X240
Length of Cable from LT Sub Panel To Distribution Board | 100 | Meter | [9 empty] | 3.5X300
R (Distribution Board) | 4.95 | Ω/Km |  |  | Ω/Km | [6 empty] | 3.5X400
X (Distribution Board) | 0 | Ω/Km |  |  | Ω/Km | [6 empty] | 3.5X500
R (Distribution Board) | 0.495 | Ω | [9 empty] | 3.5X630
X (Distribution Board) | 0 | Ω | [9 empty] | 4cX 1.5
R (Distribution Board) | 0.495 | Ω | [9 empty] | 4cX 2.5
Z p.u (F) | 3.9602 | Ω | [9 empty] | 4cX4
Total Z p.u (F) (Up to Distribution Board) | 4.1222 | Ω | [9 empty] | 4cX 6
Fault Level at Distribution Board | 0.36388 | MVA | [9 empty] | 4cX 10
Fault Current at Distribution Board | 0.48521 | Kamp | [9 empty] | 4cX16
4cX 25
4cX35
4cX 50
4cX70
4cX 95
4cX 120
4cX 150
4cX 185
4cX 240
4cX 300
4cX 400
4cX 500
4cX 630
Note on G31: Insert Cable's Reasistance/Km if You Know otherwise leave Blank
Note on G32: Insert Cable's Reactance/Km if You Know otherwise leave Blank
Note on G48: Insert Cable's Reasistance/Km if You Know otherwise leave Blank
Note on G49: Insert Cable's Reactance/Km if You Know otherwise leave Blank
Note on G61: Insert Cable's Reasistance/Km if You Know otherwise leave Blank
Note on G62: Insert Cable's Reactance/Km if You Know otherwise leave Blank
Note on G74: Insert Cable's Reasistance/Km if You Know otherwise leave Blank
Note on G75: Insert Cable's Reactance/Km if You Know otherwise leave Blank
From Power Generation
From Power Distribution T/C

## Sheet3
| mm2 | AWG/Kcmill | "C" For Copper conductor. |  |  |  | mm2 | AWG/Kcmill | "C" For Allu conductor.
|  |  | 3 Single Conductor |  | 3 Conductor Cable |  |  |  | 3 Single Conductor |  | 3 Conductor Cable
|  |  | 600V |  | 600V |  |  |  | 600V |  | 600V
|  |  | Steel | Nonmagnetic | Steel | Nonmagnetic |  |  | Steel | Nonmagnetic | Steel | Nonmagnetic
| 2.5 mm2 | 14 AWG | 389 | 389 | 389 | 389 | 2.5 mm2 | 14 AWG | 237 | 237 | 237 | 237
| 4 mm2 | 12 AWG | 617 | 617 | 617 | 617 | 4 mm2 | 12 AWG | 376 | 376 | 376 | 376
| 6 mm2 | 10 AWG | 981 | 982 | 982 | 982 | 6 mm2 | 10 AWG | 599 | 599 | 599 | 599
| 10 mm2 | 8 AWG | 1557 | 1559 | 1559 | 1560 | 10 mm2 | 8 AWG | 951 | 952 | 952 | 952
| 16 mm2 | 6 AWG | 2425 | 2430 | 2431 | 2433 | 16 mm2 | 6 AWG | 1481 | 1482 | 1482 | 1482
| 25 mm2 | 4 AWG | 3806 | 3826 | 3830 | 3838 | 25 mm2 | 4 AWG | 2346 | 2350 | 2351 | 2353
| 30 mm2 | 3 AWG | 4774 | 4811 | 4820 | 4833 | 30 mm2 | 3 AWG | 2952 | 2961 | 2963 | 2966
| 35 mm2 | 2 AWG | 5907 | 6044 | 5989 | 6087 | 35 mm2 | 2 AWG | 3713 | 3730 | 3734 | 3740
| 50 mm2 | 1 AWG | 7293 | 7493 | 7454 | 7579 | 50 mm2 | 1 AWG | 4645 | 4678 | 4686 | 4699
| 55 mm2 | O AWG | 8925 | 9317 | 9210 | 9473 | 55 mm2 | O AWG | 5777 | 5838 | 5852 | 5876
| 70 mm2 | OO AWG | 10755 | 11424 | 11245 | 11703 | 70 mm2 | OO AWG | 7187 | 7301 | 7327 | 7373
| 95 mm2 | OOO AWG | 12844 | 13923 | 13656 | 14410 | 95 mm2 | OOO AWG | 8826 | 9110 | 9077 | 9243
| 120 mm2 | OOOO AWG | 15082 | 16673 | 16392 | 17483 | 120 mm2 | OOOO AWG | 10741 | 11174 | 11185 | 11409
| 127 mm2 | 250 kcmil | 16483 | 18594 | 18311 | 19779 | 127 mm2 | 250 kcmil | 12122 | 12862 | 12797 | 13236
| 152 mm2 | 300 kcmil | 18177 | 20868 | 20617 | 22525 | 152 mm2 | 300 kcmil | 13910 | 14923 | 14917 | 15495
| 177 mm2 | 350 kcmil | 19704 | 22737 | 22646 | 24904 | 177 mm2 | 350 kcmil | 15484 | 16813 | 16795 | 17635
| 203 mm2 | 400 kcmil | 20566 | 24297 | 24253 | 26916 | 203 mm2 | 400 kcmil | 16671 | 18506 | 18462 | 19588
| 253 mm2 | 500 kcmil | 22185 | 26706 | 26980 | 30096 | 253 mm2 | 500 kcmil | 18756 | 21391 | 21395 | 23018
| 304 mm2 | 600 kcmil | 22965 | 28033 | 28752 | 32154 | 304 mm2 | 600 kcmil | 20093 | 23451 | 23633 | 25708
| 355 mm2 | 750 kcmil | 24137 | 29735 | 31051 | 34605 | 355 mm2 | 750 kcmil | 21766 | 25976 | 26432 | 29036
| 507 mm2 | 1000 kcmil | 25278 | 31491 | 33864 | 37197 | 507 mm2 | 1000 kcmil | 23478 | 28779 | 29865 | 32938
Cu
Non-Metalic | 120 mm2 |  | 15082 | 16673 | 16392 | 17483 |  |  | 10741 | 11174 | 11185 | 11409
3 Core Cable | 120 mm2 |  | 15082 | 16673 | 16392 | 17483 |  |  | 10741 | 11174 | 11185 | 11409
|  |  | 0 | 0 | 0 | 17483 |  |  | 0 | 0 | 0 | 0 | 17483
|  |  | 0 | 0 | 0 | 17483 |  |  | 0 | 0 | 0 | 0 | 17483
Cu
Non-Metalic | 30 mm2 |  | 4774 | 4811 | 4820 | 4833 |  |  | 2952 | 2961 | 2963 | 2966
3 Core Cable | 127 mm2 |  | 16483 | 18594 | 18311 | 19779 |  |  | 12122 | 12862 | 12797 | 13236
|  |  | 0 | 0 | 0 | 4833 |  |  | 0 | 0 | 0 | 0 | 4833
|  |  | 0 | 0 | 0 | 19779 |  |  | 0 | 0 | 0 | 0 | 19779
Cu
Non-Metalic | 127 mm2 |  | 16483 | 18594 | 18311 | 19779 |  |  | 12122 | 12862 | 12797 | 13236
1 Core Cable | 127 mm2 |  | 16483 | 18594 | 18311 | 19779 |  |  | 12122 | 12862 | 12797 | 13236
|  |  | 0 | 18594 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 18594
|  |  | 0 | 18594 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 18594

## Sheet5
Nominal Conductor Area (Sq.mm) | PVC Flexible
| Maximum Conductor Resistance at 20°C (ohm/km) | Maximum Conductor Reactance at 20°C (ohm/km) | Aluminium Current Carrying Capacity (Amp) | Copper Current Carrying Capacity (Amp) | Copper Current Carrying Capacity (Amp)
1cX0.5 | 39 | 0 | 4 | 4 | 0.057143
1cX0.75 | 26 | 0 | 7 | 7 | 0.1
1cX1 | 19.5 | 0 | 11 | 11 | 0.15714
1cX1.5 | 13.3 | 0 | 15 | 15 | 0.21429 | HT XLPE ( 6.6 KV-Earthed)
1cX2.5 | 7.98 | 0 | 19 | 19 | 0.27143 | 1cX35
1cX4 | 4.95 | 0 | 26 | 26 | 0.37143 | CU |  |  |  |  | PVC Flexible (Up to 1.1 KV) |  |  |  | Corrrection Factor:K1 |  |  | Ground Corrrection Factor:K2 |  |  | Corrrection Factor:K3 |  | Correction Factor(K4)(Ground Cable Dist) | [5 empty] | No of Cable/Tray | (Grouping factor)==No of Tray
1cX6 | 3.3 | 0 | 35 | 35 | 0.5 | 2 |  |  |  |  | LT PVC (Up to 1.1 KV) |  |  |  | Ambient Temp© | Insulation |  | Ground Temp© | Insulation |  | Soil Thermal Resistivity: 2.5 k.m/W |  | No of Circuit | Nill | cable Dia | 0.125m | 0.25m | 0.5m |  | 1 | 2 | 3 | 4 | 6 | 8
1cX10 | 1.91 | 0 | 46 | 46 | 0.65714 | [5 empty] | LT XLPE (Up to 1.1 KV) |  |  |  |  | PVC | XLPE/EPR |  | PVC | XLPE/EPR | Resistivity | K3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1cX16 | 1.21 | 0 | 62 | 62 | 0.88571 | [5 empty] | HT XLPE ( 6.6 KV-Earthed) |  |  |  | 10 | 1.22 | 1.15 | 10 | 1.1 | 1.07 | 1 | 1.18 | 2 | 0.75 | 0.8 | 0.85 | 0.9 | 0.9 | 2 | 0.84 | 0.8 | 0.78 | 0.77 | 0.76 | 0.75
1cX25 | 0.78 | 0 | 80 | 80 | 1.1429 | [5 empty] | HT XLPE ( 11 KV-Earthed) |  |  |  | 15 | 1.17 | 1.12 | 15 | 1.05 | 1.04 | 1.5 | 1.1 | 3 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 3 | 0.8 | 0.76 | 0.74 | 0.73 | 0.72 | 0.71
1cX35 | 0.554 | 0 | 102 | 102 | 1.4571 | [5 empty] | HT XLPE ( 11 KV-Un Earthed) |  |  |  | 20 | 1.12 | 1.08 | 20 | 0.95 | 0.96 | 2 | 1.05 | 4 | 0.6 | 0.6 | 0.7 | 0.75 | 0.8 | 4 | 0.78 | 0.74 | 0.72 | 0.71 | 0.7 | 0.69
1cX50 | 0.386 | 0 | 138 | 138 | 1.9714 | [5 empty] | HT XLPE ( 66 KV-Earthed) |  |  |  | 25 | 1.06 | 1.04 | 25 | 0.89 | 0.93 | 2.5 | 1 | 5 | 0.55 | 0.55 | 0.65 | 0.7 | 0.8 | 5 | 0.77 | 0.73 | 0.7 | 0.69 | 0.68 | 0.67
1cX70 | 0.272 | 0 | 214 | 214 | 3.0571 | [9 empty] | 35 | 0.94 | 0.96 | 35 | 0.77 | 0.89 | 3 | 0.96 | 6 | 0.5 | 0.55 | 0.6 | 0.7 | 0.8 | 6 | 0.75 | 0.71 | 0.7 | 0.68 | 0.68 | 0.66
1cX95 | 0.206 | 0 | 254 | 254 | 3.6286 |  |  |  | AL | CU | S.C |  |  |  | 40 | 0.87 | 0.91 | 40 | 0.71 | 0.85 | [8 empty] | 7 | 0.74 | 0.69 | 0.675 | 0.66 | 0.66 | 0.64
1cX120 | 0.161 | 0 | 300 | 300 | 4.2857 |  | Rsi | React | Amp | Amp |  |  |  |  | 45 | 0.79 | 0.87 | 45 | 0.63 | 0.8 | Corrrection Factor:K3 |  |  | (Temp. Derating factor) |  |  |  |  | 8 | 0.73 | 0.69 | 0.68 | 0.67 | 0.66 | 0.64
2cX0.5 | 39 | 0 | 4 | 4 | 0.057143 | PVC Flexible (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0 |  |  |  | 50 | 0.71 | 0.82 | 50 | 0.55 | 0.76 | Nature of Soil | K3 |  |  | PVC Flexible (Up to 1.1 KV) | LT PVC | LT XLPE | HT XLPE | Depth Facator (K5)
2cX0.75 | 26 | 0 | 7 | 7 | 0.1 | LT PVC (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0 |  |  |  | 55 | 0.61 | 0.76 | 55 | 0.45 | 0.71 | Very Wet Soil | 1.21 | 1 | 25 | 1.25 | 1.16 | 1.28 | 1.14 | Laying Depth(mt) | Rating Factor
2cX1 | 19.5 | 0 | 11 | 11 | 0.15714 | LT XLPE (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0 |  |  |  | 60 | 0.5 | 0.71 | 60 | 0 | 0.65 | Wet Soil | 1.13 | 2 | 30 | 1.16 | 1.1 | 1.22 | 1.1 | 0.5 | 1.1
2cX1.5 | 13.3 | 0 | 15 | 15 | 0.21429 | HT XLPE ( 6.6 KV-Earthed) | 1.1 | 0.129 | 0 | 155 | 5.00 |  |  |  | 65 | 0 | 0.65 | 65 | 0 | 0.6 | Damp Soil | 1.05 | 3 | 35 | 1.09 | 1.05 | 1.134 | 1.04 | 0.7 | 1.05
2cX2.5 | 7.98 | 0 | 19 | 19 | 0.27143 | HT XLPE ( 11 KV-Earthed) | 0 | 0 | 0 | 0 | 0 |  |  |  | 70 | 0 | 0.58 | 70 | 0 | 0.53 | Dry Soil | 1 | 4 | 40 | 1 | 1 | 1 | 1 | 0.9 | 1.01
2cX4 | 4.95 | 0 | 26 | 26 | 0.37143 | HT XLPE ( 11 KV-Un Earthed) | 0 | 0 | 0 | 0 | 0 |  |  |  | 75 | 0 | 0.5 | 75 | 0 | 0.46 | Very Dry Soil | 0.86 | 5 | 45 | 0.9 | 0.94 | 0.975 | 0.95 | 1 | 1
3cX0.5 | 39 | 0 | 4 | 4 | 0.057143 | HT XLPE ( 66 KV-Earthed) | 0 | 0 | 0 | 0 | 0 |  |  |  | 80 | 0 | 0.41 | 80 | 0 | 0.38 |  |  | 6 | 50 | 0.8 | 0.88 | 0.878 | 0.9 | 1.2 | 0.98
3cX0.75 | 26 | 0 | 7 | 7 | 0.1 | [17 empty] | 7 | 55 | 0.69 | 0.82 | 0.768 | 0.85 | 1.5 | 0.96
3cX1 | 19.5 | 0 | 11 | 11 | 0.15714 | [17 empty] | 8 | 60 | 0.62 | 0.74 | 0.658 | 0.8
3cX1.5 | 13.3 | 0 | 15 | 15 | 0.21429
3cX2.5 | 7.98 | 0 | 19 | 19 | 0.27143 | HT XLPE ( 6.6 KV-Earthed) | 1.1 | 0.129 | 155 |  | 5.00
3cX4 | 4.95 | 0 | 26 | 26 | 0.37143 |  | FALSE
HT XLPE ( 11 KV-Un Earthed)
3cX 400
CU
2
[9 empty] | AL | CL | S.C
[7 empty] | Rsi | React | Amp | Amp
[6 empty] | PVC Flexible (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT PVC (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 6.6 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Un Earthed) | 0.102 | 0.0968 | 0 | 500 | 57.20
[6 empty] | HT XLPE ( 66 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Un Earthed) | 0.102 | 0.0968 | 500 |  | 57.20
LT XLPE (Up to 1.1 KV)
3cX 95
[6 empty] | CU |  |  |  |  | PVC Flexible (Up to 1.1 KV)
[6 empty] | 2 |  |  |  |  | LT PVC (Up to 1.1 KV)
LT XLPE (Up to 1.1 KV)
HT XLPE ( 6.6 KV-Earthed)
HT XLPE ( 11 KV-Earthed)
HT XLPE ( 11 KV-Un Earthed)
HT XLPE ( 66 KV-Earthed)
[9 empty] | AL | CL | S.C
[7 empty] | Rsi | React | Amp | Amp
[6 empty] | PVC Flexible (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT PVC (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0.247 | 0.074 | 0 | 250 | 13.59
[6 empty] | HT XLPE ( 6.6 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Un Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 66 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0.247 | 0.074 | 250 |  | 13.59
LT XLPE (Up to 1.1 KV)
3.5X50
[6 empty] | CU |  |  |  |  | PVC Flexible (Up to 1.1 KV)
[6 empty] | 2 |  |  |  |  | LT PVC (Up to 1.1 KV)
LT XLPE (Up to 1.1 KV)
HT XLPE ( 6.6 KV-Earthed)
HT XLPE ( 11 KV-Earthed)
HT XLPE ( 11 KV-Un Earthed)
HT XLPE ( 66 KV-Earthed)
[9 empty] | AL | CL | S.C
[7 empty] | Rsi | React | Amp | Amp
[6 empty] | PVC Flexible (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT PVC (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0.0495 | 0.078 | 0 | 170 | 7.15
[6 empty] | HT XLPE ( 6.6 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Un Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 66 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0.0495 | 0.078 | 170 |  | 7.15
PVC Flexible (Up to 1.1 KV)
1cX4
[6 empty] | CU |  |  |  |  | PVC Flexible (Up to 1.1 KV)
[6 empty] | 2 |  |  |  |  | LT PVC (Up to 1.1 KV)
LT XLPE (Up to 1.1 KV)
HT XLPE ( 6.6 KV-Earthed)
HT XLPE ( 11 KV-Earthed)
HT XLPE ( 11 KV-Un Earthed)
HT XLPE ( 66 KV-Earthed)
[9 empty] | AL | CU | S.C
[7 empty] | Rsi | React | Amp | Amp
[6 empty] | PVC Flexible (Up to 1.1 KV) | 4.95 | 0 | 26 | 26 | 0.37143
[6 empty] | LT PVC (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | LT XLPE (Up to 1.1 KV) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 6.6 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 11 KV-Un Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | HT XLPE ( 66 KV-Earthed) | 0 | 0 | 0 | 0 | 0
[6 empty] | PVC Flexible (Up to 1.1 KV) | 4.95 | 0 | 26 |  | 0.37143
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Nominal Conductor Area (Sq.mm) | 1.1 KV PVC Insulated | [11 empty] | 1.1 KV XLPE Insulated
| Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps |  | Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps
| Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper | Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper
| ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp |  |  | ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp
1cX4 | 8.8 | 0.158 | 5.52 | 0.0158 | — | — | — | 39 | 38 | 35 | 0.304 | 0.460 | 1.555 | 0.102 | 1.555 | 0.102 | — | — | — | 48 | 47 | 45 | 0.376 | 0.572
1cX6 | 5.53 | 0.148 | 3.69 | 0.148 | 39 | 37 | 35 | 49 | 48 | 44 | 0.456 | 0.690 | 1.553 | 0.102 | 1.553 | 0.102 | 48 | 45 | 45 | 60 | 59 | 57 | 0.564 | 0.858
1cX10 | 3.7 | 0.138 | 2.19 | 0.138 | 51 | 51 | 47 | 65 | 64 | 60 | 0.760 | 1.150 | 1.553 | 0.102 | 1.553 | 0.102 | 62 | 62 | 61 | 80 | 78 | 77 | 0.940 | 1.430
1cX16 | 2.29 | 0.128 | 1.38 | 0.128 | 66 | 65 | 64 | 85 | 83 | 82 | 1.220 | 1.84 | 1.54 | 0.102 | 1.54 | 0.102 | 81 | 80 | 83 | 104 | 102 | 106 | 1.504 | 2.288
1cX25 | 1.44 | 0.12 | 0.87 | 0.12 | 86 | 84 | 84 | 110 | 110 | 110 | 1.900 | 2.88 | 1.54 | 0.102 | 0.93 | 0.102 | 99 | 90 | 115 | 130 | 115 | 145 | 2.350 | 3.575
1cX35 | 1.04 | 0.114 | 0.627 | 0.114 | 100 | 100 | 105 | 130 | 125 | 130 | 2.660 | 4.03 | 1.11 | 0.097 | 0.671 | 0.097 | 117 | 110 | 135 | 155 | 140 | 175 | 3.290 | 5.005
1cX50 | 0.77 | 0.11 | 0.463 | 0.11 | 120 | 115 | 130 | 155 | 150 | 165 | 3.800 | 5.75 | 0.82 | 0.092 | 0.495 | 0.092 | 138 | 125 | 170 | 185 | 165 | 215 | 4.700 | 7.150
1cX70 | 0.53 | 0.103 | 0.321 | 0.103 | 140 | 135 | 155 | 190 | 175 | 205 | 5.320 | 8.05 | 0.56 | 0.088 | 0.343 | 0.088 | 168 | 155 | 210 | 225 | 200 | 270 | 6.580 | 10.01
1cX95 | 0.38 | 0.101 | 0.231 | 0.101 | 175 | 155 | 190 | 220 | 200 | 245 | 7.220 | 10.90 | 0.41 | 0.085 | 0.247 | 0.085 | 204 | 185 | 255 | 265 | 235 | 330 | 8.930 | 13.59
1cX120 | 0.3 | 0.096 | 0.184 | 0.096 | 195 | 170 | 220 | 250 | 220 | 280 | 9.120 | 13.80 | 0.32 | 0.082 | 0.196 | 0.082 | 230 | 210 | 300 | 300 | 265 | 380 | 11.28 | 17.16
1cX150 | 0.25 | 0.094 | 0.149 | 0.094 | 220 | 190 | 250 | 280 | 245 | 320 | 11.40 | 17.30 | 0.265 | 0.082 | 0.159 | 0.082 | 265 | 230 | 342 | 335 | 300 | 430 | 14.10 | 21.45
1cX185 | 0.2 | 0.092 | 0.12 | 0.092 | 240 | 210 | 290 | 305 | 260 | 370 | 14.10 | 21.30 | 0.211 | 0.082 | 0.127 | 0.082 | 295 | 260 | 385 | 380 | 335 | 495 | 17.39 | 26.46
1cX240 | 0.15 | 0.09 | 0.091 | 0.09 | 270 | 225 | 335 | 345 | 285 | 425 | 18.20 | 27.30 | 0.162 | 0.079 | 0.0965 | 0.079 | 340 | 300 | 450 | 435 | 385 | 590 | 22.56 | 34.32
1cX300 | 0.12 | 0.088 | 0.074 | 0.088 | 295 | 245 | 380 | 375 | 310 | 475 | 22.80 | 34.50 | 0.13 | 0.078 | 0.0769 | 0.078 | 390 | 335 | 519 | 490 | 430 | 670 | 28.20 | 42.90
1cX400 | 0.094 | 0.088 | 0.059 | 0.088 | 325 | 275 | 435 | 400 | 335 | 550 | 30.40 | 46.00 | 0.1023 | 0.077 | 0.0608 | 0.077 | 450 | 380 | 605 | 550 | 480 | 780 | 37.60 | 57.20
1cX 500 | 0.0726 | 0.087 | 0.046 | 0.087 | 345 | 295 | 480 | 425 | 355 | 590 | 38.00 | 57.50 | 0.0808 | 0.076 | 0.0468 | 0.076 | 500 | 430 | 700 | 610 | 530 | 900 | 47.00 | 71.50
1cX 630 | 0.0563 | 0.086 | 0.037 | 0.086 | 390 | 320 | 550 | 470 | 375 | 660 | 47.90 | 72.50 | 0.0648 | 0.075 | 0.0362 | 0.075 | 555 | 485 | 809 | 680 | 590 | 1020 | 59.22 | 90.09
1cX800 | 0.044 | 0.083 | 0.031 | 0.083 | 450 | 380 | 610 | 530 | 425 | 725 | 60.80 | 92.00 | 0.053 | 0.075 | 0.0283 | 0.075 | 625 | 530 | 935 | 740 | 630 | 1140 | 75.20 | 114.40
1cX1000 | 0.0349 | 0.082 | 0.027 | 0.082 | 500 | 415 | 680 | 590 | 740 | 870 | 76.00 | 115.00 | 0.0444 | 0.068 | 0.0225 | 0.068 | 690 | 570 | 1065 | 780 | 660 | 1250 | 94.00 | 143.00
2cX1.5 | 21.72 | 0.126 | 14.5 | 0.126 | 18 | 16 | 16 | 23 | 20 | 20 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
2cX2.5 | 14.52 | 0.119 | 8.87 | 0.119 | 16 | 21 | 21 | 32 | 27 | 27 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
2cX4 | 8.89 | 0.116 | 5.52 | 0.116 | 32 | 27 | 27 | 41 | 35 | 35 | 0.304 | 0.460 | 1.555 | 0.097 | 1.555 | 0.097 | 34 | 28 | 30 | 44 | 37 | 39 | 0.376 | 0.572
2cX 6 | 5.53 | 0.11 | 3.69 | 0.11 | 40 | 34 | 35 | 50 | 44 | 45 | 0.456 | 0.690 | 1.553 | 0.097 | 1.553 | 0.097 | 43 | 37 | 40 | 55 | 47 | 50 | 0.564 | 0.858
2cX10 | 3.7 | 0.1 | 2.19 | 0.1 | 55 | 45 | 47 | 70 | 58 | 60 | 0.760 | 1.150 | 1.553 | 0.085 | 1.553 | 0.085 | 57 | 48 | 53 | 74 | 61 | 67 | 0.940 | 1.430
2cX16 | 2.29 | 0.097 | 1.38 | 0.097 | 70 | 58 | 59 | 90 | 75 | 78 | 1.220 | 1.840 | 1.54 | 0.08 | 1.54 | 0.08 | 78 | 61 | 70 | 94 | 78 | 85 | 1.50 | 2.29
2cX25 | 1.44 | 0.097 | 0.87 | 0.097 | 90 | 76 | 78 | 115 | 97 | 105 | 1.900 | 2.880 | 1.54 | 0.08 | 0.93 | 0.08 | 95 | 80 | 99 | 120 | 100 | 125 | 2.35 | 3.58
2cX35 | 1.04 | 0.097 | 0.627 | 0.097 | 110 | 92 | 99 | 140 | 120 | 125 | 2.660 | 4.030 | 1.11 | 0.08 | 0.671 | 0.08 | 116 | 94 | 117 | 145 | 120 | 155 | 3.29 | 5.01
2cX50 | 0.77 | 0.094 | 0.463 | 0.094 | 135 | 115 | 125 | 165 | 145 | 155 | 3.800 | 5.750 | 0.082 | 0.078 | 0.495 | 0.078 | 140 | 110 | 140 | 170 | 145 | 190 | 4.70 | 7.15
2cX70 | 0.53 | 0.09 | 0.321 | 0.09 | 160 | 140 | 150 | 205 | 180 | 195 | 5.320 | 8.050 | 0.57 | 0.077 | 0.343 | 0.077 | 170 | 140 | 176 | 210 | 175 | 235 | 6.58 | 10.01
2cX95 | 0.38 | 0.09 | 0.231 | 0.9 | 190 | 170 | 185 | 240 | 215 | 230 | 7.220 | 10.90 | 0.41 | 0.074 | 0.247 | 0.074 | 200 | 165 | 221 | 250 | 210 | 290 | 8.93 | 13.59
2cX120 | 0.3 | 0.087 | 0.184 | 0.087 | 210 | 190 | 210 | 275 | 235 | 265 | 9.120 | 13.80 | 0.33 | 0.072 | 0.196 | 0.072 | 225 | 185 | 258 | 285 | 240 | 330 | 11.28 | 17.16
2cX150 | 0.25 | 0.087 | 0.149 | 0.087 | 240 | 210 | 240 | 310 | 270 | 305 | 11.40 | 17.300 | 0.27 | 0.072 | 0.159 | 0.072 | 255 | 210 | 294 | 315 | 270 | 375 | 14.10 | 21.45
2cX185 | 0.2 | 0.087 | 0.12 | 0.087 | 275 | 240 | 275 | 350 | 300 | 350 | 14.10 | 21.280 | 0.21 | 0.072 | 0.127 | 0.072 | 285 | 235 | 339 | 355 | 300 | 435 | 17.39 | 26.46
2cX240 | 0.15 | 0.087 | 0.091 | 0.087 | 320 | 275 | 325 | 405 | 345 | 410 | 18.20 | 27.600 | 0.16 | 0.072 | 0.0965 | 0.072 | 325 | 270 | 402 | 410 | 350 | 510 | 22.56 | 34.32
2cX300 | 0.12 | 0.086 | 0.073 | 0.086 | 355 | 305 | 365 | 450 | 385 | 465 | 22.80 | 34.500 | 0.13 | 0.071 | 0.0769 | 0.071 | 370 | 305 | 461 | 460 | 390 | 590 | 28.20 | 42.90
2cX400 | 0.09 | 0.086 | 0.059 | 0.086 | 385 | 345 | 420 | 490 | 485 | 530 | 30.40 | 46.000 | 0.1 | 0.07 | 0.0602 | 0.07 | 435 | 350 | 542 | 520 | 440 | 670 | 37.60 | 57.20
2cX500 | 0.09 | 0.086 | 0.059 | 0.086 | 425 | 380 | 475 | 540 | 460 | 605 | 38.00 | 57.500 | 0.1 | 0.07 | 0.0602 | 0.07 | 481 | 405 | 624 | 580 | 480 | 750 | 47.00 | 71.50
2cX630 | 0.09 | 0.086 | 0.059 | 0.086 | 465 | 415 | 540 | 640 | 550 | 785 | 47.90 | 72.550 | 0.1 | 0.07 | 0.0602 | 0.07 | 537 | 470 | 723 | 680 | 575 | 875 | 59.22 | 90.09
3cX1.5 | 21.72 | 0.126 | 14.5 | 0.126 | 16 | 14 | 13 | 21 | 17 | 17 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
3cX2.5 | 14.52 | 0.119 | 8.87 | 0.119 | 21 | 18 | 18 | 27 | 24 | 24 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
3cX4 | 8.89 | 0.116 | 5.52 | 0.116 | 28 | 23 | 23 | 36 | 30 | 30 | 0.304 | 0.460 | 1.581 | 0.097 | 1.581 | 0.097 | 34 | 28 | 30 | 44 | 37 | 39 | 0.376 | 0.572
3cX 6 | 5.53 | 0.11 | 3.69 | 0.11 | 35 | 30 | 30 | 45 | 38 | 39 | 0.456 | 0.690 | 1.57 | 0.097 | 1.57 | 0.097 | 43 | 37 | 40 | 55 | 47 | 50 | 0.564 | 0.858
3cX 10 | 3.7 | 0.1 | 2.19 | 0.1 | 46 | 39 | 40 | 60 | 50 | 52 | 0.760 | 1.150 | 1.55 | 0.08 | 1.55 | 0.08 | 57 | 48 | 53 | 74 | 61 | 67 | 0.940 | 1.430
3cX 16 | 2.29 | 0.097 | 1.38 | 0.097 | 60 | 50 | 51 | 77 | 64 | 66 | 1.220 | 1.840 | 1.557 | 0.08 | 1.557 | 0.08 | 78 | 61 | 70 | 94 | 78 | 85 | 1.50 | 2.29
3cX 25 | 1.44 | 0.097 | 0.87 | 0.097 | 76 | 63 | 70 | 99 | 81 | 90 | 1.900 | 2.880 | 1.54 | 0.08 | 0.93 | 0.08 | 95 | 80 | 99 | 120 | 100 | 125 | 2.35 | 3.58
3cX 35 | 1.04 | 0.097 | 0.627 | 0.097 | 92 | 77 | 86 | 120 | 99 | 110 | 2.660 | 4.030 | 1.11 | 0.08 | 0.671 | 0.08 | 116 | 94 | 117 | 145 | 120 | 155 | 3.29 | 5.01
3cX 50 | 0.77 | 0.094 | 0.463 | 0.094 | 110 | 95 | 105 | 145 | 125 | 135 | 3.800 | 5.750 | 0.082 | 0.078 | 0.495 | 0.078 | 140 | 110 | 140 | 170 | 145 | 190 | 4.70 | 7.15
3cX 70 | 0.53 | 0.09 | 0.321 | 0.09 | 135 | 115 | 130 | 175 | 150 | 165 | 5.320 | 8.050 | 0.57 | 0.077 | 0.343 | 0.077 | 170 | 140 | 176 | 210 | 175 | 235 | 6.58 | 10.01
3cX 95 | 0.38 | 0.9 | 0.231 | 0.09 | 165 | 140 | 155 | 210 | 175 | 200 | 7.220 | 10.900 | 0.41 | 0.074 | 0.247 | 0.074 | 200 | 165 | 221 | 250 | 210 | 290 | 8.93 | 13.59
3cX 120 | 0.3 | 0.087 | 0.184 | 0.087 | 185 | 155 | 180 | 240 | 195 | 230 | 9.120 | 13.800 | 0.33 | 0.072 | 0.196 | 0.072 | 225 | 185 | 258 | 285 | 240 | 330 | 11.28 | 17.16
3cX 150 | 0.25 | 0.087 | 0.149 | 0.087 | 210 | 175 | 205 | 270 | 225 | 265 | 11.40 | 17.300 | 0.27 | 0.072 | 0.159 | 0.072 | 255 | 210 | 294 | 315 | 270 | 375 | 14.10 | 21.45
3cX 185 | 0.2 | 0.087 | 0.12 | 0.087 | 235 | 200 | 240 | 300 | 255 | 305 | 14.10 | 21.300 | 0.21 | 0.072 | 0.127 | 0.072 | 285 | 235 | 339 | 355 | 300 | 435 | 17.39 | 26.46
3cX 240 | 0.15 | 0.087 | 0.0912 | 0.087 | 275 | 235 | 280 | 345 | 295 | 355 | 18.20 | 27.600 | 0.16 | 0.072 | 0.0965 | 0.072 | 325 | 270 | 402 | 410 | 350 | 510 | 22.56 | 34.32
3cX 300 | 0.12 | 0.086 | 0.0739 | 0.086 | 305 | 260 | 315 | 385 | 335 | 400 | 22.80 | 34.500 | 0.13 | 0.071 | 0.0769 | 0.071 | 370 | 305 | 461 | 460 | 390 | 590 | 28.20 | 42.90
3cX 400 | 0.09 | 0.086 | 0.0592 | 0.086 | 335 | 290 | 375 | 425 | 360 | 435 | 30.40 | 46.000 | 0.1 | 0.07 | 0.0602 | 0.07 | 435 | 350 | 542 | 520 | 440 | 670 | 37.60 | 57.20
3cX 500 | 0.09 | 0.086 | 0.0592 | 0.086 | 370 | 320 | 425 | 470 | 390 | 520 | 38.00 | 57.500 | 0.1 | 0.07 | 0.0602 | 0.07 | 481 | 405 | 624 | 580 | 480 | 750 | 47.00 | 71.50
3cX 630 | 0.09 | 0.086 | 0.0592 | 0.086 | 405 | 350 | 480 | 555 | 470 | 675 | 47.90 | 72.500 | 0.1 | 0.07 | 0.0602 | 0.07 | 537 | 470 | 723 | 680 | 575 | 875 | 59.22 | 90.09
3.5X16 | 1.44 | 0.097 | 0.73 | 0.097 | 70 | 65 | 62 | 99 | 81 | 90 | 1.8 | 2.5 | — | — | — | — | — | — | — | — | — | — | — | —
3.5X25 | 0.77 | 0.094 | 0.387 | .0.094 | 76 | 63 | 70 | 99 | 81 | 90 | 1.90 | 2.88 | 1.54 | 0.08 | 0.93 | 0.08 | 95 | 80 | 99 | 120 | 100 | 125 | 2.35 | 3.58
3.5X35 | 0.53 | 0.09 | 0.268 | 0.09 | 92 | 77 | 86 | 120 | 99 | 110 | 2.66 | 4.03 | 1.11 | 0.08 | 0.671 | 0.08 | 116 | 94 | 117 | 145 | 120 | 155 | 3.29 | 5.01
3.5X50 | 0.38 | 0.09 | 0.193 | 0.09 | 110 | 95 | 105 | 145 | 125 | 135 | 3.80 | 5.75 | 0.082 | 0.078 | 0.0495 | 0.078 | 140 | 110 | 140 | 170 | 145 | 190 | 4.70 | 7.15
3.5X70 | 0.3 | 0.087 | 0.153 | 0.087 | 135 | 115 | 130 | 175 | 150 | 165 | 5.32 | 8.05 | 0.57 | 0.077 | 0.343 | 0.077 | 170 | 140 | 176 | 210 | 175 | 235 | 6.58 | 10.01
3.5X95 | 0.2 | 0.087 | 0.099 | 0.087 | 165 | 140 | 155 | 210 | 175 | 200 | 7.22 | 10.90 | 0.41 | 0.074 | 0.247 | 0.074 | 200 | 165 | 221 | 250 | 210 | 290 | 8.93 | 13.59
3.5X120 | 0.15 | 0.087 | 0.075 | 0.087 | 185 | 155 | 180 | 240 | 195 | 230 | 9.12 | 13.80 | 0.33 | 0.072 | 0.196 | 0.072 | 225 | 185 | 258 | 285 | 240 | 330 | 11.28 | 17.16
3.5X150 | 0.12 | 0.086 | 0.06 | 0.086 | 210 | 175 | 205 | 270 | 225 | 265 | 11.40 | 17.30 | 0.27 | 0.072 | 0.159 | 0.072 | 255 | 210 | 294 | 315 | 270 | 375 | 14.10 | 21.45
3.5X185 | 0.09 | 0.086 | 0.047 | 0.086 | 235 | 200 | 240 | 300 | 255 | 305 | 14.10 | 21.30 | 0.21 | 0.072 | 0.127 | 0.072 | 285 | 235 | 339 | 355 | 300 | 435 | 17.39 | 26.46
3.5X240 | 0.08 | 0.085 | 0.046 | 0.085 | 275 | 235 | 280 | 345 | 295 | 355 | 18.20 | 27.60 | 0.16 | 0.072 | 0.0965 | 0.072 | 325 | 270 | 402 | 410 | 350 | 510 | 22.56 | 34.32
3.5X300 | 0.08 | 0.085 | 0.046 | 0.085 | 305 | 260 | 315 | 385 | 335 | 400 | 22.80 | 34.50 | 0.13 | 0.071 | 0.0769 | 0.071 | 370 | 305 | 461 | 460 | 390 | 590 | 28.20 | 42.90
3.5X400 | 0.08 | 0.084 | 0.045 | 0.084 | 335 | 290 | 375 | 425 | 360 | 435 | 30.40 | 46.00 | 0.1 | 0.07 | 0.0602 | 0.07 | 435 | 350 | 542 | 520 | 440 | 670 | 37.60 | 57.20
3.5X500 | 0.08 | 0.084 | 0.045 | 0.084 | 370 | 320 | 425 | 470 | 390 | 520 | 38.00 | 57.50 | 0.1 | 0.07 | 0.0602 | 0.07 | 481 | 405 | 624 | 580 | 480 | 750 | 47.00 | 71.50
3.5X630 | 0.08 | 0.084 | 0.045 | 0.084 | 405 | 350 | 480 | 555 | 470 | 675 | 47.90 | 72.50 | 0.1 | 0.07 | 0.0602 | 0.07 | 537 | 470 | 723 | 680 | 575 | 875 | 59.22 | 90.09
4cX 1.5 | 21.72 | 0.126 | 14.5 | 0.126 | 16 | 14 | 13 | 21 | 17 | 17 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
4cX 2.5 | 14.52 | 0.119 | 8.87 | 0.119 | 21 | 18 | 18 | 27 | 24 | 24 | 0.3 | 0.4 | — | — | — | — | — | — | — | — | — | — | — | —
4cX4 | 8.89 | 0.116 | 5.52 | 0.116 | 28 | 23 | 23 | 36 | 30 | 30 | 0.304 | 0.460 | 5.53 | 0.11 | 3.69 | 0.11 | 34 | 28 | 30 | 44 | 37 | 39 | 0.376 | 0.572
4cX 6 | 5.53 | 0.11 | 3.69 | 0.11 | 35 | 30 | 30 | 45 | 38 | 39 | 0.456 | 0.690 | 3.7 | 0.1 | 2.19 | 0.1 | 43 | 37 | 40 | 55 | 47 | 50 | 0.564 | 0.858
4cX 10 | 3.7 | 0.1 | 2.19 | 0.1 | 46 | 39 | 40 | 60 | 50 | 52 | 0.760 | 1.150 | 2.29 | 0.097 | 1.38 | 0.097 | 57 | 48 | 53 | 74 | 61 | 67 | 0.940 | 1.430
4cX16 | 2.29 | 0.097 | 1.38 | 0.097 | 60 | 50 | 51 | 77 | 64 | 66 | 1.220 | 1.840 | 2.45 | 0.08 | 1.47 | 0.08 | 78 | 61 | 70 | 94 | 78 | 85 | 1.50 | 2.29
4cX 25 | 1.44 | 0.097 | 0.87 | 0.097 | 76 | 63 | 70 | 99 | 81 | 90 | 1.900 | 2.880 | 1.54 | 0.08 | 0.93 | 0.08 | 95 | 80 | 99 | 120 | 100 | 125 | 2.35 | 3.58
4cX35 | 1.04 | 0.097 | 0.62 | 0.097 | 92 | 77 | 86 | 120 | 99 | 110 | 2.660 | 4.030 | 1.11 | 0.08 | 0.671 | 0.08 | 116 | 94 | 117 | 145 | 120 | 155 | 3.29 | 5.01
4cX 50 | 0.77 | 0.094 | 0.46 | 0.094 | 110 | 95 | 105 | 145 | 125 | 135 | 3.800 | 5.750 | 0.082 | 0.078 | 0.495 | 0.078 | 140 | 110 | 140 | 170 | 145 | 190 | 4.70 | 7.15
4cX70 | 0.53 | 0.09 | 0.32 | 0.09 | 135 | 115 | 130 | 175 | 150 | 165 | 5.320 | 8.050 | 0.57 | 0.077 | 0.343 | 0.077 | 170 | 140 | 176 | 210 | 175 | 235 | 6.58 | 10.01
4cX 95 | 0.38 | 0.9 | 0.23 | 0.09 | 165 | 140 | 155 | 210 | 175 | 200 | 7.220 | 10.900 | 0.41 | 0.074 | 0.247 | 0.074 | 200 | 165 | 221 | 250 | 210 | 290 | 8.93 | 13.59
4cX 120 | 0.3 | 0.087 | 0.18 | 0.087 | 185 | 155 | 180 | 240 | 195 | 230 | 9.120 | 13.800 | 0.33 | 0.072 | 0.196 | 0.072 | 225 | 185 | 258 | 285 | 240 | 330 | 11.28 | 17.16
4cX 150 | 0.25 | 0.087 | 0.14 | 0.087 | 210 | 175 | 205 | 270 | 225 | 265 | 11.400 | 17.300 | 0.27 | 0.072 | 0.159 | 0.072 | 255 | 210 | 294 | 315 | 270 | 375 | 14.10 | 21.45
4cX 185 | 0.2 | 0.087 | 0.12 | 0.087 | 235 | 200 | 240 | 300 | 255 | 305 | 14.100 | 21.300 | 0.21 | 0.072 | 0.127 | 0.072 | 285 | 235 | 339 | 355 | 300 | 435 | 17.39 | 26.46
4cX 240 | 0.15 | 0.087 | 0.091 | 0.087 | 275 | 235 | 280 | 345 | 295 | 355 | 18.200 | 27.600 | 0.16 | 0.072 | 0.0965 | 0.072 | 325 | 270 | 402 | 410 | 350 | 510 | 22.56 | 34.32
4cX 300 | 0.12 | 0.086 | 0.073 | 0.086 | 305 | 260 | 315 | 385 | 335 | 400 | 22.800 | 34.500 | 0.13 | 0.071 | 0.0769 | 0.071 | 370 | 305 | 461 | 460 | 390 | 590 | 28.20 | 42.90
4cX 400 | 0.09 | 0.086 | 0.059 | 0.086 | 335 | 290 | 375 | 425 | 360 | 435 | 30.400 | 46.000 | 0.1 | 0.07 | 0.0602 | 0.07 | 435 | 350 | 542 | 520 | 440 | 670 | 37.60 | 57.20
4cX 500 | 0.09 | 0.086 | 0.059 | 0.086 | 370 | 320 | 425 | 470 | 390 | 520 | 38.000 | 57.500 | 0.1 | 0.07 | 0.0602 | 0.07 | 481 | 405 | 624 | 580 | 480 | 750 | 47.00 | 71.50
4cX 630 | 0.09 | 0.086 | 0.059 | 0.086 | 405 | 350 | 480 | 555 | 470 | 675 | 47.900 | 72.500 | 0.1 | 0.07 | 0.0602 | 0.07 | 537 | 470 | 723 | 680 | 575 | 875 | 59.22 | 90.09
Nominal Conductor Area (Sq.mm) | 3.8 / 6.6 KV(6.6 KV Earthed) AL/COPPER COND, XLPE INSULATED CABLES
| Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps
| Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper
| ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp
1cX25 | 1.1 | 0.129 | 1.1 | 0.129 | 100 | 90 | 120 | 130 | 115 | 155 | 2.35 | 3.58
1cX35 | 1.1 | 0.129 | 1.1 | 0.129 | 120 | 105 | 145 | 155 | 140 | 185 | 3.29 | 5.00
1cX50 | 0.822 | 0.1293 | 0.822 | 0.1293 | 140 | 125 | 170 | 185 | 160 | 220 | 4.70 | 7.15
1cX70 | 0.568 | 0.1195 | 0.568 | 0.1195 | 175 | 155 | 215 | 225 | 195 | 275 | 6.58 | 10.01
1cX95 | 0.411 | 0.113 | 0.411 | 0.113 | 205 | 180 | 260 | 265 | 235 | 340 | 8.93 | 13.59
1cX120 | 0.325 | 0.1085 | 0.325 | 0.1085 | 235 | 205 | 305 | 300 | 265 | 390 | 11.28 | 17.16
1cX150 | 0.265 | 0.1062 | 0.265 | 0.1062 | 260 | 230 | 345 | 335 | 295 | 440 | 14.10 | 21.45
1cX185 | 0.211 | 0.1025 | 0.211 | 0.1025 | 295 | 260 | 395 | 380 | 330 | 510 | 17.39 | 26.46
1cX240 | 0.161 | 0.1011 | 0.161 | 0.1011 | 340 | 300 | 470 | 435 | 380 | 600 | 22.56 | 34.32
1cX300 | 0.13 | 0.0988 | 0.13 | 0.0988 | 385 | 335 | 540 | 490 | 425 | 680 | 28.20 | 42.90
1cX400 | 0.102 | 0.0959 | 0.102 | 0.0959 | 0.57 | 440 | 380 | 630 | 550 | 480 | 790 | 37.60
1cX 500 | 0.08 | 0.0936 | 0.08 | 0.0936 | 0.60 | 495 | 430 | 730 | 610 | 530 | 910 | 47.00
1cX 630 | 0.063 | 0.0919 | 0.063 | 0.0919 | 0.67 | 560 | 480 | 840 | 680 | 580 | 1030 | 59.22
1cX800 | 0.0513 | 0.0895 | 0.0513 | 0.0895 | 0.76 | 620 | 530 | 960 | 740 | 630 | 1140 | 75.20
1cX1000 | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 0.82 | 680 | 580 | 1070 | 790 | 670 | 1250 | 94.00
3cX 25 | 1.1 | 0.134 | 1.1 | 0.134 | 95 | 82 | 105 | 120 | 105 | 135 | 2.35 | 3.58
3cX 35 | 1.1 | 0.134 | 1.1 | 0.134 | 115 | 97 | 125 | 145 | 125 | 165 | 3.29 | 5.01
3cX 50 | 0.822 | 0.1358 | 0.822 | 0.1358 | 130 | 115 | 150 | 170 | 150 | 195 | 4.70 | 7.15
3cX 70 | 0.568 | 0.1237 | 0.568 | 0.1237 | 160 | 140 | 190 | 210 | 180 | 240 | 6.58 | 10.01
3cX 95 | 0.411 | 0.1168 | 0.411 | 0.1168 | 190 | 165 | 230 | 250 | 215 | 295 | 8.93 | 13.59
3cX 120 | 0.325 | 0.1128 | 0.325 | 0.1128 | 220 | 190 | 260 | 280 | 240 | 335 | 11.28 | 17.16
3cX 150 | 0.265 | 0.1096 | 0.265 | 0.1096 | 245 | 210 | 295 | 310 | 270 | 380 | 14.10 | 21.45
3cX 185 | 0.211 | 0.1073 | 0.211 | 0.1073 | 275 | 240 | 335 | 350 | 305 | 430 | 17.39 | 26.46
3cX 240 | 0.161 | 0.1041 | 0.161 | 0.1041 | 315 | 275 | 395 | 400 | 350 | 500 | 22.56 | 34.32
3cX 300 | 0.13 | 0.1002 | 0.13 | 0.1002 | 355 | 310 | 450 | 445 | 390 | 570 | 28.20 | 42.90
3cX 400 | 0.102 | 0.0968 | 0.102 | 0.0968 | 400 | 350 | 520 | 500 | 440 | 650 | 37.60 | 57.20
Nominal Conductor Area (Sq.mm) | 6.6 /11 KV(6.6KV Un-Earthed/11KV Earthed) AL/COPPER COND, XLPE INSULATED CABLES
| Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps
| Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper
| ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp
1cX25 | 1.1 | 0.134 | 1.1 | 0.134 | 100 | 90 | 120 | 130 | 115 | 155 | 2.35 | 3.58
1cX35 | 1.1 | 0.134 | 1.1 | 0.134 | 120 | 105 | 145 | 155 | 140 | 185 | 3.29 | 5.00
1cX50 | 0.822 | 0.1358 | 0.822 | 0.1358 | 140 | 125 | 170 | 185 | 160 | 220 | 4.70 | 7.15
1cX70 | 0.568 | 0.1237 | 0.568 | 0.1237 | 175 | 155 | 215 | 225 | 195 | 275 | 6.58 | 10.01
1cX95 | 0.411 | 0.1168 | 0.411 | 0.1168 | 205 | 180 | 260 | 265 | 235 | 340 | 8.93 | 13.59
1cX120 | 0.325 | 0.1128 | 0.325 | 0.1128 | 235 | 205 | 305 | 300 | 265 | 390 | 11.28 | 17.16
1cX150 | 0.265 | 0.1096 | 0.265 | 0.1096 | 260 | 230 | 345 | 335 | 295 | 440 | 14.10 | 21.45
1cX185 | 0.211 | 0.1073 | 0.211 | 0.1073 | 295 | 260 | 395 | 380 | 330 | 510 | 17.39 | 26.46
1cX240 | 0.161 | 0.1041 | 0.161 | 0.1041 | 340 | 300 | 470 | 435 | 380 | 600 | 22.56 | 34.32
1cX300 | 0.13 | 0.1002 | 0.13 | 0.1002 | 385 | 335 | 540 | 490 | 425 | 680 | 28.20 | 42.90
1cX400 | 0.102 | 0.0968 | 0.102 | 0.0968 | 440 | 380 | 630 | 550 | 480 | 790 | 37.60 | 57.20
1cX 500 | 0.08 | 0.0939 | 0.08 | 0.0939 | 495 | 430 | 730 | 610 | 530 | 910 | 47.00 | 71.50
1cX 630 | 0.063 | 0.0921 | 0.063 | 0.0921 | 560 | 480 | 840 | 680 | 580 | 1030 | 59.22 | 90.10
1cX800 | 0.0513 | 0.097 | 0.0513 | 0.097 | 620 | 530 | 960 | 740 | 630 | 1140 | 75.20 | 114.40
1cX1000 | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 680 | 580 | 1070 | 790 | 670 | 1250 | 94.00 | 143.00
3cX 25 | 1.1 | 0.134 | 1.1 | 0.134 | 95 | 82 | 105 | 120 | 105 | 135 | 2.35 | 3.58
3cX 35 | 1.1 | 0.134 | 1.1 | 0.134 | 115 | 97 | 125 | 145 | 125 | 165 | 3.29 | 5.01
3cX 50 | 0.822 | 0.1358 | 0.822 | 0.1358 | 130 | 115 | 150 | 170 | 150 | 195 | 4.70 | 7.15
3cX 70 | 0.568 | 0.1237 | 0.568 | 0.1237 | 160 | 140 | 190 | 210 | 180 | 240 | 6.58 | 10.01
3cX 95 | 0.411 | 0.1168 | 0.411 | 0.1168 | 190 | 165 | 230 | 250 | 215 | 295 | 8.93 | 13.59
3cX 120 | 0.325 | 0.1128 | 0.325 | 0.1128 | 220 | 190 | 260 | 280 | 240 | 335 | 11.28 | 17.16
3cX 150 | 0.265 | 0.1096 | 0.265 | 0.1096 | 245 | 210 | 295 | 310 | 270 | 380 | 14.10 | 21.45
3cX 185 | 0.211 | 0.1073 | 0.211 | 0.1073 | 275 | 240 | 335 | 350 | 305 | 430 | 17.39 | 26.46
3cX 240 | 0.161 | 0.1041 | 0.161 | 0.1041 | 315 | 275 | 395 | 400 | 350 | 500 | 22.56 | 34.32
3cX 300 | 0.13 | 0.1002 | 0.13 | 0.1002 | 355 | 310 | 450 | 445 | 390 | 570 | 28.20 | 42.90
3cX 400 | 0.102 | 0.0968 | 0.102 | 0.0968 | 400 | 350 | 520 | 500 | 440 | 650 | 37.60 | 57.20
Nominal Conductor Area (Sq.mm) | 11 KV(11KV Un Earthed) AL/COPPER COND, XLPE INSULATED CABLES
| Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps
| Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper
| ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp
1cX25 | 1.1 | 0.134 | 1.1 | 0.134 | 100 | 90 | 120 | 130 | 115 | 155 | 2.35 | 3.58
1cX35 | 1.1 | 0.134 | 1.1 | 0.134 | 120 | 105 | 145 | 155 | 140 | 185 | 3.29 | 5.00
1cX50 | 0.822 | 0.1358 | 0.822 | 0.1358 | 140 | 125 | 170 | 185 | 160 | 220 | 4.70 | 7.15
1cX70 | 0.568 | 0.1237 | 0.568 | 0.1237 | 175 | 155 | 215 | 225 | 195 | 275 | 6.58 | 10.01
1cX95 | 0.411 | 0.1168 | 0.411 | 0.1168 | 205 | 180 | 260 | 265 | 235 | 340 | 8.93 | 13.59
1cX120 | 0.325 | 0.1128 | 0.325 | 0.1128 | 235 | 205 | 305 | 300 | 265 | 390 | 11.28 | 17.16
1cX150 | 0.265 | 0.1096 | 0.265 | 0.1096 | 260 | 230 | 345 | 335 | 295 | 440 | 14.10 | 21.45
1cX185 | 0.211 | 0.1073 | 0.211 | 0.1073 | 295 | 260 | 395 | 380 | 330 | 510 | 17.39 | 26.46
1cX240 | 0.161 | 0.1041 | 0.161 | 0.1041 | 340 | 300 | 470 | 435 | 380 | 600 | 22.56 | 34.32
1cX300 | 0.13 | 0.1002 | 0.13 | 0.1002 | 385 | 335 | 540 | 490 | 425 | 680 | 28.20 | 42.90
1cX400 | 0.102 | 0.0968 | 0.102 | 0.0968 | 440 | 380 | 630 | 550 | 480 | 790 | 37.60 | 57.20
1cX 500 | 0.08 | 0.0939 | 0.08 | 0.0939 | 495 | 430 | 730 | 610 | 530 | 910 | 47.00 | 71.50
1cX 630 | 0.063 | 0.0921 | 0.063 | 0.0921 | 560 | 480 | 840 | 680 | 580 | 1030 | 59.22 | 90.10
1cX800 | 0.0513 | 0.097 | 0.0513 | 0.097 | 620 | 530 | 960 | 740 | 630 | 1140 | 75.20 | 114.40
1cX1000 | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 680 | 580 | 1070 | 790 | 670 | 1250 | 94.00 | 143.00
3cX 25 | 1.1 | 0.134 | 1.1 | 0.134 | 95 | 82 | 105 | 120 | 105 | 135 | 2.35 | 3.58
3cX 35 | 1.1 | 0.134 | 1.1 | 0.134 | 115 | 97 | 125 | 145 | 125 | 165 | 3.29 | 5.01
3cX 50 | 0.822 | 0.1358 | 0.822 | 0.1358 | 130 | 115 | 150 | 170 | 150 | 195 | 4.70 | 7.15
3cX 70 | 0.568 | 0.1237 | 0.568 | 0.1237 | 160 | 140 | 190 | 210 | 180 | 240 | 6.58 | 10.01
3cX 95 | 0.411 | 0.1168 | 0.411 | 0.1168 | 190 | 165 | 230 | 250 | 215 | 295 | 8.93 | 13.59
3cX 120 | 0.325 | 0.1128 | 0.325 | 0.1128 | 220 | 190 | 260 | 280 | 240 | 335 | 11.28 | 17.16
3cX 150 | 0.265 | 0.1096 | 0.265 | 0.1096 | 245 | 210 | 295 | 310 | 270 | 380 | 14.10 | 21.45
3cX 185 | 0.211 | 0.1073 | 0.211 | 0.1073 | 275 | 240 | 335 | 350 | 305 | 430 | 17.39 | 26.46
3cX 240 | 0.161 | 0.1041 | 0.161 | 0.1041 | 315 | 275 | 395 | 400 | 350 | 500 | 22.56 | 34.32
3cX 300 | 0.13 | 0.1002 | 0.13 | 0.1002 | 355 | 310 | 450 | 445 | 390 | 570 | 28.20 | 42.90
3cX 400 | 0.102 | 0.0968 | 0.102 | 0.0968 | 400 | 350 | 520 | 500 | 440 | 650 | 37.60 | 57.20
Nominal Conductor Area (Sq.mm) | 66 KV(66 KV Un Earthed) AL/COPPER COND, XLPE INSULATED CABLES
| Aluminium |  | Copper |  | Aluminum |  |  | Copper |  |  | Short Circuit Current Rating for 1Sec.duration in K. Amps
| Resi | React | Resi | React | Ground | Duct | Air | Ground | Duct | Air | Aluminium | Copper
| ohm/km | ohm/km | ohm/km | ohm/km | Amp | Amp | Amp | Amp | Amp | Amp
1cX 95 | 0.32 | 0.219 |  |  | 195 | 240 | 240 |  |  |  | 9.8
1cX120 | 0.253 | 0.218 |  |  | 220 | 280 | 280 |  |  |  | 12.4
1cX150 | 0.206 | 0.217 |  |  | 240 | 335 | 335 |  |  |  | 15.5
1cX185 | 0.164 | 0.215 |  |  | 275 | 380 | 380 |  |  |  | 19.2
1cX240 | 0.125 | 0.2 |  |  | 320 | 450 | 450 |  |  |  | 24.8
1cX300 | 0.1 | 0.19 |  |  | 360 | 510 | 510 |  |  |  | 31.1
1cX400 | 0.778 | 0.181 |  |  | 410 | 595 | 595 |  |  |  | 41.4
1cX 500 | 0.0605 | 0.183 |  |  | 460 | 690 | 690 |  |  |  | 51.8
1cX 630 | 0.0469 | 0.183 |  |  | 525 | 800 | 800 |  |  |  | 65.2
1cX800 | 0.0367 | 0.183 |  |  | 590 | 910 | 910 |  |  |  | 82.8
1cX1000 | 0.0291 | 0.183 |  |  | 650 | 1010 | 1010 |  |  |  | 104