## Starter
[5 empty] | Jignesh.parmar www.electricalnotes.wordpress.com jiguparmar@yahoo.com | [5 empty] | Jignesh.parmar www.electricalnotes.wordpress.com jiguparmar@yahoo.com
| System Voltage | 415 | Volt |  |  |  | System Voltage | 415 | Volt
| Phase | 3 Phase | 3 |  |  |  | Phase | 3 Phase | 3
| Type of Motor | 3 Phase Induction |  |  |  |  | Type of Motor | 3 Phase Induction
| Motor Size | 5 | HP | 3.73 | 5 |  | Motor Size | 10 | HP | 7.46 | 10
| Motor Code | A |  |  |  |  | Motor Code | A
| Motor Efficiency | 80% |  |  |  |  | Motor Efficiency | 100%
| Motor RPM | 750 |  |  |  |  | Motor RPM | 600
| System P.F | 0.8 |  |  |  |  | System P.F | 0.8
| Application of Motor | Motor Load in Household Application |  |  |  |  | Application of Motor | Non-Inductive or Slightly Inductive ,Resistive Load
| Place of Over Load Relay | In the line (Putting the overload before the motor) |  |  |  |  | Place of Over Load Relay | In the windings (overload is placed after the Winding Split in to main and delta Contactor) |  |  |  | 0
| Motor Torque / Current | [5 empty] | Motor Starting / Full Load Current
| Motor Rated Tourque (Full Load): | 35.0133 | lb-ft | (5252xHpxRPM) |  |  | Motor Rated Tourque (Full Load) | 87.5333 | lb-ft | (5252xHpxRPM)
| Motor Rated Tourque (Full Load): | 47.4953 | Nm | (9500xKw/RPM) |  |  | Motor Rated Tourque | 118.7383 | Nm | (9500xKw/RPM)
| Motor Starting Torque: | 142.486 | Nm |  |  |  | Motor Starting Torque | 356.215 | Nm
| Lock Rotor Current IL(Min): | 6.9562 | Amp |  |  |  | Lock Rotor Current IL(Min): | 13.9125 | Amp
| Lock Rotor Current IL(Max): | 21.8426 | Amp |  |  |  | Lock Rotor Current IL(Max): | 43.6851 | Amp
| Motor Starting Current : | 45.4068 | Amp | (6 to 7 x Full Load Current) |  |  | Motor Starting Current : | 38.9201 | Amp | (3x Full Load Current)
| Motor Full Load Current (Line): | 6.4867 | Amp |  |  |  | Motor Full Load Current (Line): | 12.9734 | Amp
| Motor Full Load Current (Phase): | 3.7452 | Amp |  |  |  | Motor Full Load Current (Phase): | 7.4904 | Amp
| Fuse (As per NEC 430-52) | [5 empty] | Fuse (As per NEC 430-52)
| Non-Time Delay Fuse (Max) | 19.4601 | Amp | (3 x full Load Current ) |  | 3 | Non-Time Delay Fuse (Max) | 38.9201 | Amp | (3 x full Load Current ) |  | 3
| Time Delay Fuse (Max) | 11.3517 | Amp | (1.75 x full Load Current ) |  | 1.75 | Time Delay Fuse (Max) | 22.7034 | Amp | (1.75 x full Load Current ) |  | 1.75
| Circuit Breaker (As per NEC 430-52) | [5 empty] | Circuit Breaker (As per NEC 430-52)
| Instantaneous Trip Circuit Breaker (Max) | 51.8935 | Amp | (8 x full Load Current ) |  | 8 | Instantaneous Trip Circuit Breaker (Max) | 103.787 | Amp | (8 x full Load Current ) |  | 8
| Inverse Time Circuit Breaker (Max) | 16.2167 | Amp | (2.5 x full Load Current ) |  | 2.5 | Inverse Time Circuit Breaker (Max) | 32.4334 | Amp | (2.5 x full Load Current ) |  | 2.5
| Over Load Relay Setting | [5 empty] | Over Load Relay Setting
| Relay Min (70% of FLC Phase): | 2.6216 | Amp |  |  |  | Relay Min (70% of FLC Phase): | 5.2433 | Amp
| Relay Max (120% of FLC Phase): | 4.4942 | Amp |  |  |  | Relay Max (120% of FLC Phase): | 8.9885 | Amp
| OR | [5 empty] | OR
| Relay Setting (100% of FLC Line): | 6.4867 | Amp |  |  |  | Relay Setting (58% of FLC Line): | 7.5246 | Amp
| Contactor | [5 empty] | Contactor
| Type of Contactor: | AC7b |  |  |  |  | Type of Contactor: | AC1
| Making / Breaking Capacity of Contactor: | 51.8935 | Amp |  |  |  | Making / Breaking Capacity of Contactor: | 19.4601 | Amp
| Main Contactor (100% of FLC Line): | 6.4867 | Amp |  |  |  | Main Contactor (58% of FLC Line): | 7.5246 | Amp | (1/√3 Full Load Current) | (Start,Transition,Running)
[7 empty] | Delta Contactor (58% of FLC Line): | 7.5246 | Amp | (1/√3 Full Load Current) | (Running)
[7 empty] | Star Contactor (33% of FLC Line): | 4.2812 | Amp | (1/3 Full Load Current) | (Start)
[14 empty] | Time Delay Fuse | Non-Time Delay Fuse | Instantaneous Trip | Inverse Time
[7 empty] | Transient Time Delay Setting | 30ms |  |  |  |  | Single Phase | 300% | 175% | 800% | 250%
[13 empty] | 3 Phase Induction | 300% | 175% | 800% | 250%
[13 empty] | Synchronous | 300% | 175% | 800% | 250%
[13 empty] | Wound Rotor | 150% | 150% | 800% | 150%
[13 empty] | Direct Current | 150% | 150% | 200% | 150%
16 | 3.31 | [5 empty] | 3.31
| 3.7 | [5 empty] | 3.7
| 4.6 | [5 empty] | 4.6
2.944 | 0.37 | [5 empty] | 0.37
| 2.95 | [5 empty] | 2.95
1 Phase
3 Phase
HP
KW
Single Phase
3 Phase Induction
Synchronous
Wound Rotor
Direct Current
| Application | Contactor | Making Cap
| Non-Inductive or Slightly Inductive ,Resistive Load | AC1 | 1.5
| Slip Ring Motor | AC2 | 4
| Squirrel Cage Motor | AC3 | 10
| Rapid Start / Stop | AC4 | 12
| Switching of Electrical Discharge Lamp | AC5a | 3
| Switching of Electrical Incandescent Lamp | AC5b | 1.5
| Switching of Transformer | AC6a | 12
| Switching of Capacitor Bank | AC6b | 12
| Slightly Inductive Load in Household or same type load | AC7a | 1.5
| Motor Load in Household Application | AC7b | 8
| Hermetic refrigerant Compressor Motor with Manual O/L Reset | AC8a | 6
| Hermetic refrigerant Compressor Motor with Auto O/L Reset | AC8b | 6
| Control of Restive & Solid State Load with optocoupler Isolation | AC12 | 6
| Control of Restive Load and Solid State with T/C Isolation | AC13 | 10
| Control of Small Electro Magnetic Load ( <72VA) | AC14 | 6
| Control of Small Electro Magnetic Load ( >72VA) | AC15 | 10
In the line (Putting the overload before the motor same as in DOL)
In the windings (overload is placed after the Winding Split in to main and delta Contactor)
| Code | Min | Max
| A | 1 | 3.14 | 1 | 3.14
| B | 3.15 | 3.54 | 1 | 3.14
| C | 3.55 | 3.99
| D | 4 | 4.49
| E | 4.5 | 4.99
| F | 5 | 2.59
| G | 2.6 | 6.29
| H | 6.3 | 7.09
| I | 7.1 | 7.99
| K | 8 | 8.99
| L | 9 | 9.99
| M | 10 | 11.19
| N | 11.2 | 12.49
| P | 12.5 | 13.99
| R | 14 | 15.99
| S | 16 | 17.99
| T | 18 | 19.99
| U | 20 | 22.39
| V | 22.4
DOL STARTER
STAR-DELTA STARTER

## Contactor Configuration
ARRANGEMENT OF MAIN CONTACTOR & AUXILIARY CONTACTOR
MAIN CONTACTOR | [18 empty] | AUXILIARY CONTECTOR | [10 empty] | SUMMARY OF CONTACTOR
MAIN CONTACTOR: 1-2, 3-4, 5-6
| 1 NO | [7 empty] | 1 NC | [10 empty] | 3NO + 1NC |  |  |  |  | 1NO + 1NC |  |  |  |  | AUXILARY CONTACTOR: (NO) : 13-14, 33-34, 43-44, 53-54, 83-84
| 1 | 3 | 5 | 13 |  |  |  |  | 1 | 3 | 5 | 21 | [7 empty] | 13 | 33 |  | 43 | 21 | 21 | 13 |  |  |  | AUXILARY CONTACTOR: (NC) : 21-22, 31-32, 41-42, 61-62, 71-72
NB: You can easily identify Whether Contactor is NO , NC from above Summary
| 2 | 4 | 6 | 14 |  |  |  |  | 2 | 4 | 6 | 22 | [7 empty] | 14 | 34 |  | 44 | 22 | 22 | 14
| NO:13-14 | [7 empty] | NC:21-22 | [10 empty] | NO:13-14, 33-34, 43-44 |  |  |  |  | NO:13-14
[20 empty] | NC:21-22 |  |  |  |  | NC:21-22
| 1 NO + 1NC | [7 empty] | 2 NO + 1NC | [10 empty] | 2NO + 2NC |  |  |  |  | 1NO + 1NC
| 1 | 3 | 5 | 13 | 21 |  |  |  | 1 | 3 | 5 | 13 | 21 | 43 |  | 31 |  |  |  | 13 | 21 | 31 | 43 |  | 43 |  | 31
| 2 | 4 | 6 | 14 | 22 |  |  |  | 2 | 4 | 6 | 14 | 22 | 44 |  | 32 |  |  |  | 14 | 22 | 32 | 44 |  | 44 |  | 32
| NO:13-14 | [7 empty] | NO:13-14, 43-44 | [10 empty] | NO:13-14, 43-44 |  |  |  |  | NO:43-44
| NC:21-22 | [7 empty] | NC:21-22, 31-32 | [10 empty] | NC:21-22, 31-32 |  |  |  |  | NC:31-32
| 2 NO + 3NC | [7 empty] | 2 NO + 1NC | [10 empty] | 2NO + 2NC |  |  |  |  | 2NO + 2NC
| 1 | 3 | 5 | 13 | 21 | 31 | 41 | 53 | 1 | 3 | 5 | 13 | 43 |  | 53 |  | 21 | 31 |  | 53 | 61 | 71 | 83 |  | 53 |  | 61 | 71 | 83
| 2 | 4 | 6 | 14 | 22 | 32 | 42 | 54 | 2 | 4 | 6 | 14 | 44 |  | 54 |  | 22 | 32 |  | 54 | 62 | 72 | 84 |  | 54 |  | 62 | 72 | 84
| NO:13-14, 53-54 | [7 empty] | NO:13-14, 43-44, 53-54 | [10 empty] | NO:53-54. 83-84 |  |  |  |  | NO:53-54, 83-84
| NC:21-22, 31-32, 41-42 | [7 empty] | NC:21-22, 31-32 | [10 empty] | NC:61-62, 71-72 |  |  |  |  | NC:61-62, 71-72
| 2 NO + 2NC | [18 empty] | 1NO + 3NC
| 1 | 3 | 5 | 13 | 21 | 31 | 43 | [12 empty] | 13 | 21 | 31 | 41
| 2 | 4 | 6 | 14 | 22 | 32 | 44 | [12 empty] | 14 | 22 | 32 | 42
| NO:13-14, 43-44 | [18 empty] | NO:13-14
| NC:21-22, 31-32 | [18 empty] | NC:21-22, 31-32, 41-42